## Prices
Medupi Power Station - Water Treatment Plant Life Cycle Cost Comparisons (Estimates only) |  |  |  | 3.85 | Used as multiplier to update costs from Majuba
The cost comparisons are based on an "all-membrane" treatment vs an ion exchange system for demineralised water production at 320 m3/h. Pretreatment is assumed to be UF in both cases
Schedule of Costs
Capital Costs for Equipment | Pricing | Comments
Primary Demineralisation Ion Exchange System | 30000000 | See IX sheet - UF-cation-degas-anion-MB (based on 2006 cost of similar plant in UK - £ 2 500 000 - @ £ 1.00 = R 14.00) This covers only cation - degas - anion part
Reverse Osmosis System | 36000000 | See RO sheet - UF - RO - RO - EDI - GTM - NRMBIX (basis - UK cost comparison vs above IX = +10% - added 10% on top)
Ultrafiltration System | 30000000
Secondary Polishing regenerable Mixed Bed Ion Exchange (MBIX) | 5000000 | IX Polisher
Electrodeionisation (EDI) Stack System | 10500000 | RO-RO Polisher
GTM System | 9000000 | Based on quotation for Grootvlei PS
Non-regen MBIX | 1800000 | Taken as 5% of RO system
Bulk Chemical Storage and Dilution a) | 1000000 | For RO - only small storage facility (delivery by liquid tote) and dilution
Bulk Chemical Storage and Dilution b) | 2187500 | For IX -attributable cost (rest to CPP) based on usage = 87.5%
Bulk Chemical Off-loading Bay | 8750000 | For IX -attributable cost (rest to CPP) based on usage = 87.5%
Regenerant and Conditioning Chemical Costs | Pricing | Comments
Sulphuric Acid, H2SO4 | 0.55 | per kg as 96% (ex Lethabo PS)
Sodium Hydroxide, NaOH | 3.47 | per kg as 50% (ex Lethabo PS))
Sodium Metabisulfite (SMBS) | 3.38 | per kg (ex Lethabo PS)
Sodium Chloride, NaCl - brine washing | 0.693 | per kg - Low magnesium salt (ex Lethabo PS)
Soda Ash | 2.3 | per kg (bags) (ex Lethabo PS)
Hydrated Lime | 0.82 | per kg (bulk) (ex Lethabo PS)
Ferric Chloride | 0.98 | per kg (bulk) (ex Lethabo PS)
Zetafloc A50 | 9.31 | per kg (ex Lethabo PS)
Zetafloc 2300 | 4.67 | per kg (ex Lethabo PS)
Anhydrous Ammonia | 3.1 | per kg (bulk) (ex Lethabo PS)
Liquid Chlorine | 7.63 | per kg (925 kg cylinder) (ex Lethabo PS)
Chlorine | 11.69 | per kg (68 kg cylinder) (ex Lethabo PS)
Nitrogen | 8 | per kg (120 kg cylinder)
Biocide (BL 8072) | 21.75 | per kg (ex Lethabo PS)
Biocide (BL 6026A) | 13.99 | per kg (ex Lethabo PS)
Biocide (781) | 38.1 | per kg (ex Lethabo PS)
Biocide (2881) | 104.2 | per kg (ex Lethabo PS)
MSI 310 | 41.74 | per kg (ex Lethabo PS)
Hydrochloric Acid | 1.07 | per kg (230 kg drums) (ex Lethabo PS)
Citric Acid | 7.57 | per kg (ex Lethabo PS)
Oxalic Acid | 5.28 | per kg (ex Lethabo PS)
EDTA | 13.79 | per kg (ex Lethabo PS)
Caustic Soda | 2.18 | per kg (310 kg drums (ex Lethabo PS)
HTH dry chlorine | 13.66 | per kg (ex Lethabo PS)
Antiscalant | 42 | per kg (ex Lethabo PS)
Cleaning-in-place chemicals | 15000 | per clean (ex Lethabo PS)
Raw Water | 2.772 | per m3 (ex Lethabo PS)
Demin Water | 3.003 | per m3 (ex Lethabo PS)
Power Costs | Pricing | Comments
Works (Internal) Power | 0.564 | per kWh | 20%
Other Consumables | Pricing | Comments
Reverse osmosis (RO) membranes | 3707 | per membrane element (ex Lethabo PS)
Ultrafiltration (UF) membranes | 34650 | per membrane element - based on MF element costs (ex Lethabo PS)
Cation Resin : Amberjet 1500 H | 21.26 | per litre resin - for CPP; from Rohm and Haas (ex Lethabo PS)
Anion Resin : Ambersep 900 OH | 42.66 | per litre resin - for CPP; from Rohm and Haas (ex Lethabo PS)
Cation Resin SAC : Amberjet 1500 H | 21.26 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Cation Resin SAC : Amberjet 1200 Na | 12.65 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Cation Resin WAC : Amberlite IRC 86 SB | 35.07 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Anion Resin SBA : Amberjet 4200 Cl | 29.61 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Anion Resin WBA : Amberlite IRA 96 | 30.3 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Inert Resin S3TR | 50 | per litre resin - for Demin; from Rohm and Haas
Cation Resin : Amberjet 1500 H | 21.26 | per litre resin - for Demin MB; from Rohm and Haas (ex Lethabo PS)
Anion Resin : Ambersep 900 OH | 42.66 | per litre resin - for Demin MB; from Rohm and Haas (ex Lethabo PS)
Labour Costs | Pricing | Comments
Manpower Recovery Rate | 220 | per hour (manpower level assumed to be CCL)
Calculation Parameters
Base Date | 2010
Design Life End Date | 2045
Project Life | 35 | years
Discount Rate | 8 | %
Escalation Rate | 7.65 | %
Based on Main Plant Availability = | 90%
demineralised water production | 320 | m3/h
demineralised water use | 0.023 | l/kwh
Capacity | 4764
Net Capacity | 4334
Note: Assumed 1st start mid 2010 - Operational costs for 2010 halved
Total Overnight Cost, ZAR/kW | 17519 | 6x750 MW, No FGD
% WTP | 0.3277%
| 1.0999 | 2008ZAR -> 2010ZAR
CRF | 0.085803
retrobuild factor (cost multiplier of plant expansion) | 1.2
Note on A77: Eskom data for Medupi

## Prices-Summary
Schedule of Costs
Capital Costs for Equipment | Pricing | Comments
Primary Demineralisation Ion Exchange System | 30000000 | See IX sheet - UF-cation-degas-anion-MB (based on 2006 cost of similar plant in UK - £ 2 500 000 - @ £ 1.00 = R 14.00) This covers only cation - degas - anion part
Reverse Osmosis System | 36000000 | See RO sheet - UF - RO - RO - EDI - GTM - NRMBIX (basis - UK cost comparison vs above IX = +10% - added 10% on top)
Ultrafiltration System | 30000000
Secondary Polishing regenerable Mixed Bed Ion Exchange (MBIX) | 5000000 | IX Polisher
Electrodeionisation (EDI) Stack System | 10500000 | RO-RO Polisher
GTM System | 9000000 | Based on quotation for Grootvlei PS
Non-regen MBIX | 1800000 | Taken as 5% of RO system
Bulk Chemical Storage and Dilution a) | 1000000 | For RO - only small storage facility (delivery by liquid tote) and dilution
Bulk Chemical Storage and Dilution b) | 2187500 | For IX -attributable cost (rest to CPP) based on usage = 87.5%
Bulk Chemical Off-loading Bay | 8750000 | For IX -attributable cost (rest to CPP) based on usage = 87.5%
Regenerant and Conditioning Chemical Costs | Pricing | Comments
Sulphuric Acid, H2SO4 | 0.55 | per kg as 96% (ex Lethabo PS)
Sodium Hydroxide, NaOH | 3.47 | per kg as 50% (ex Lethabo PS))
Sodium Metabisulfite (SMBS) | 3.38 | per kg (ex Lethabo PS)
Sodium Chloride, NaCl - brine washing | 0.693 | per kg - Low magnesium salt (ex Lethabo PS)
Soda Ash | 2.3 | per kg (bags) (ex Lethabo PS)
Hydrated Lime | 0.82 | per kg (bulk) (ex Lethabo PS)
Ferric Chloride | 0.98 | per kg (bulk) (ex Lethabo PS)
Zetafloc A50 | 9.31 | per kg (ex Lethabo PS)
Zetafloc 2300 | 4.67 | per kg (ex Lethabo PS)
Anhydrous Ammonia | 3.1 | per kg (bulk) (ex Lethabo PS)
Liquid Chlorine | 7.63 | per kg (925 kg cylinder) (ex Lethabo PS)
Chlorine | 11.69 | per kg (68 kg cylinder) (ex Lethabo PS)
Nitrogen | 8 | per kg (120 kg cylinder)
Biocide (BL 8072) | 21.75 | per kg (ex Lethabo PS)
Biocide (BL 6026A) | 13.99 | per kg (ex Lethabo PS)
Biocide (781) | 38.1 | per kg (ex Lethabo PS)
Biocide (2881) | 104.2 | per kg (ex Lethabo PS)
MSI 310 | 41.74 | per kg (ex Lethabo PS)
Hydrochloric Acid | 1.07 | per kg (230 kg drums) (ex Lethabo PS)
Citric Acid | 7.57 | per kg (ex Lethabo PS)
Oxalic Acid | 5.28 | per kg (ex Lethabo PS)
EDTA | 13.79 | per kg (ex Lethabo PS)
Caustic Soda | 2.18 | per kg (310 kg drums (ex Lethabo PS)
HTH dry chlorine | 13.66 | per kg (ex Lethabo PS)
Antiscalant | 42 | per kg (ex Lethabo PS)
Cleaning-in-place chemicals | 15000 | per clean (ex Lethabo PS)
Raw Water | 2.772 | per m3 (ex Lethabo PS)
Demin Water | 3.003 | per m3 (ex Lethabo PS)
Power Costs | Pricing | Comments
Works (Internal) Power | 0.15 | per kWh
Other Consumables | Pricing | Comments
Reverse osmosis (RO) membranes | 3707 | per membrane element (ex Lethabo PS)
Ultrafiltration (UF) membranes | 34650 | per membrane element - based on MF element costs (ex Lethabo PS)
Cation Resin : Amberjet 1500 H | 21.26 | per litre resin - for CPP; from Rohm and Haas (ex Lethabo PS)
Anion Resin : Ambersep 900 OH | 42.66 | per litre resin - for CPP; from Rohm and Haas (ex Lethabo PS)
Cation Resin SAC : Amberjet 1500 H | 21.26 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Cation Resin SAC : Amberjet 1200 Na | 12.65 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Cation Resin WAC : Amberlite IRC 86 SB | 35.07 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Anion Resin SBA : Amberjet 4200 Cl | 29.61 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Anion Resin WBA : Amberlite IRA 96 | 30.3 | per litre resin - for Demin; from Rohm and Haas (ex Lethabo PS)
Inert Resin S3TR | 50 | per litre resin - for Demin; from Rohm and Haas
Cation Resin : Amberjet 1500 H | 21.26 | per litre resin - for Demin MB; from Rohm and Haas (ex Lethabo PS)
Anion Resin : Ambersep 900 OH | 42.66 | per litre resin - for Demin MB; from Rohm and Haas (ex Lethabo PS)
Labour Costs | Pricing | Comments
Manpower Recovery Rate | 220 | per hour (manpower level assumed to be CCL)
Calculation Parameters
Base Date | 2010
Design Life End Date | 2045
Project Life | 35 | years
Discount Rate | 12.5 | %
Escalation Rate | 7.65 | %
Based on Main Plant Availability = | 90%
Note: Assumed 1st start mid 2010 - Operational costs for 2010 halved

## RO-Mo
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 1:
Membrane-based System: Double Pass Reverse Osmosis; Water Source - Mokolo System Only Configuration : Raw → UF → RO 1st Pass → RO 2nd Pass → EDI → GTM → NRMB
Results | [5 empty] | 0.564 | R/kwh | 2.4728 | kWh/m3 | 0.80808 | System EFF
Net Present Value this Scenario |  |  |  | 248820813.927 |  | 10.6337 | /m3 | 3.8361 | demin$:raw$ | 57.4114 | R/kW (gross)
[6 empty] | 11.6958 | 2010ZAR
Manpower: | [5 empty] | RO Plant Data: | [13 empty] | Chemical usage :
Number of Chemist/Operators for WTP per shift |  |  | 1 |  |  | Number of array stages in 1st Pass |  |  | 3 |  |  |  | Number of array stages in 2nd Pass |  |  | 3 |  |  |  | Pass 1 pH adjustment |  |  | acid |  |  | Pass 2 pH adjustment |  |  | caustic
Number of Shifts per day |  |  | 3 | [5 empty] | 1st Stage | 2nd Stage | 3rd Stage |  |  |  |  | 1st Stage | 2nd Stage | 3rd Stage |  | Pass 1 Dose rate (as 100% chemical) |  |  | 37.7 | mg/L |  | Pass 2 Dose rate (as 100% chemical) |  |  | 27.29 | mg/L
Duration of shift |  |  | 9 | hours |  | Number of pressure vessels 1st Pass |  |  | 32 | 16 | 8 |  | Number of pressure vessels 2nd Pass |  |  | 30 | 16 | 8 |  | Pass 1 pH adjustment Chemical usage (as 100% chemical) |  |  | 14.9292 | kg/h |  | Pass 2 pH adjustment Chemical usage (as 100% chemical) |  |  | 10.8068 | kg/h
Average time spent per shift on demin plant |  |  | 2 | hours |  | Number of membrane elements per pressure vessel |  |  | 6 | 6 | 6 |  | Number of membrane elements per pressure vessel |  |  | 6 | 6 | 6 |  |  |  |  | 117701.8128 | kg p a |  |  |  |  | 85201.1266 | kg p a
Fraction of shift time spent on demin plant (average) |  |  | 22.22% |  |  | Number of membrane elements per stage |  |  | 192 | 96 | 48 |  | Number of membrane elements per stage |  |  | 180 | 96 | 48 |  | Annualised pH adjustment Chemical cost - Pass 1 |  |  | 64735.997 |  |  | Annualised pH adjustment Chemical cost - Pass 2 |  |  | 147823.9546
Number of days per annum |  |  | 365 | days |  | Total number of membrane elements in 1st Pass |  |  | 336 |  |  |  | Total number of membrane elements in 2nd Pass |  |  | 324 |  |  |  | Pass 1 Antiscalant |  |  | for BaSO4 |  |  | Pass 2 Antiscalant |  |  | nil
Plant availability |  |  | 90% |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Pass 1Antiscalant Dose rate (as 100% chemical) |  |  | 0.5 | mg/L |  | Pass 2Antiscalant Dose rate (as 100% chemical) |  |  | 0 | mg/L
Number of operating days |  |  | 328.5 | days |  | Membrane Replacement cost |  |  | 1245552 |  |  |  | Membrane Replacement cost |  |  | 1201068 |  |  |  | Pass 1 Antiscalant Chemical usage (as 100% chemical) |  |  | 0.198 | kg/h |  | Pass 2 Antiscalant Chemical usage (as 100% chemical) |  |  | 0 | kg/h
Number of manhours per annum on demin plant |  |  | 1752 | hours |  | Pass 1 Feed Flow |  |  | 396 | m3/h |  |  | Pass 2 Feed Flow |  |  | 369 | m3/h | [5 empty] | 1561.032 | kg p a |  |  |  |  | 0 | kg p a
Annualised Labour Cost |  |  | 385440 |  |  | Pass 1 Product (permeate) Flow |  |  | 352.95 | m3/h |  |  | Pass 2 Product (permeate) Flow |  |  | 335.4 | m3/h |  |  | Annualised Antiscalant cost - Pass 1 |  |  | 65563.344 |  |  | Annualised Antiscalant cost - Pass 2 |  |  | 0
[6 empty] | Pass 1 Reject (concentrate) Flow |  |  | 43.05 | m3/h |  |  | Pass 2 Reject (concentrate) Flow (recycled to Pass 1) |  |  | 33.6 | m3/h |  |  | Pass 1 Dechlorination |  |  | SMBS |  |  | Pass 2 Dechlorination |  |  | nil
[6 empty] | Pass 1 Recovery |  |  | 89.13% |  |  |  | Pass 2 Recovery |  |  | 90.89% |  |  |  | Pass 1 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L |  | Pass 2 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L
[6 empty] | Pass 1 Average flux |  |  | 25.7 | Lmh |  |  | Pass 2 Average flux |  |  | 25.32 | Lmh |  |  | Pass 1 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h |  | Pass 2 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h
20 yr | 248820813.927 |  |  |  | 551.19 | Pass 1 power consumption |  |  | 315.95 | kW |  |  | Pass 2 power consumption |  |  | 235.24 | kW | [5 empty] | 0 | kg p a |  |  |  |  | 0 | kg p a
35yr | 363923757.0345 |  |  |  | 2450908.2254 | Pass 1 Annualised power cost |  |  | 1404895.6872 |  |  |  | Pass 2 Annualised power cost |  |  | 1046012.5382 |  |  |  | Annualised Dechlorination cost - Pass 1 |  |  | 0 |  |  | Annualised Dechlorination cost - Pass 2 |  |  | 0
power cost | 3518531.123
[6 empty] | RO Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | EDI Plant Data : |  |  |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data :
[6 empty] | Raw Water Usage for demin production |  | 3122064 | m3 per annum | raw water cost: | Flow to UF plant |  | 255.5 | m3/h |  | EDI Feed flow |  | 336 | m3/h |  | Cation Resin Volume |  | 2.5 | m3 |  | Flow through GTM |  | 320 | m3/h
[6 empty] | Annualised Raw Water cost |  | 0 |  | 0 | Number of UF pressure vessels housings |  | 24 |  |  | EDI Demin production flow |  | 320 | m3/h |  | Anion Resin Volume |  | 2.5 | m3 |  | Number of Skids (parallel operation) |  | 6
[6 empty] | Average equivalent weight of influent stream |  | 26 | g/equiv | 8654361.408 | Number of UF elements per housing |  | 4 |  |  | EDI Concentrate flow (recycled to 2nd Pass RO) |  | 16 | m3/h |  | Resin Replacement Frequency |  | 2 | years |  | GTM Contactors per skid (series operation) |  | 4
[6 empty] | TDS of RO influent stream |  | 92.8 | mg/L (as ions) |  | Total number of UF elements |  | 96 |  |  | EDI Recovery |  | 95.24% |  |  | Cation Resin Replacement Cost |  | 53150 |  |  | Total number of contactors |  | 24
[8 empty] | 3.5692 | meq/L |  | UF Element replacement Cost |  | 3326400 |  |  | EDI power requirement |  | 0.74 | kWh/m3 |  | Anion Resin Replacement Cost |  | 106650 |  |  | Frequency of GTM replacement |  | 7 | years
[6 empty] | Cleaning-in-place (CIP) Frequency |  | 4 | per annum |  | UF element replacement frequency |  | 5 | years |  |  |  | 1960277.76 | kWh p a | [6 empty] | Cost of GTM Replacement |  | 4419000
[6 empty] | Annualised CIP costs |  | 60000 |  |  | UF system Recovery |  | 92.9 | % |  | Annualised EDI power cost |  | 1105596.6566 | [7 empty] | Nitrogen sweep rate |  | 7.5 | Nm3/h
[6 empty] | Volume of effluent produced |  | 339406.2 | m3 per annum |  | UF System Backwash water |  | 18.1405 | m3/h |  | EDI Stack replacement frequency |  | 8 | years | [6 empty] | Nitrogen usage per annum |  | 59130 | Nm3
[6 empty] | Average equivalent weight of influent stream |  | 26 | g/equiv |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | EDI Stack replacement costs (60% of new) |  | 6300000 | [7 empty] | Annualised usage @ 1.1455 kg/m3 @ NTP |  | 51619.3802 | kg
[6 empty] | TDS of RO reject stream |  | 841 | mg/L (as ions) |  | UF Power Requirement |  | 0.2 | kWh/m3 | [11 empty] | Annualised N2 costs |  | 412955.0415
[8 empty] | 32.3462 | meq/L |  | Annualised UF Power Usage |  | 402872.4 | kWh | [11 empty] | Power requirement for GTM |  | 189 | kW
[6 empty] | Effluent solids loading per annum |  | 10978485.1615 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 | [12 empty] | Annualised GTM power usage |  | 1490076 | kWh
[8 empty] | 548.9243 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d | [11 empty] | Annualised GTM power costs |  | 840402.864
[13 empty] | 1090.62 | L per annum
[11 empty] | Annualised CEB NaOCl cost |  | 14897.8692
[11 empty] | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[13 empty] | 1304.145 | L per annum
[11 empty] | Annualised CEB HCl cost |  | 930.2901
Events/Activities |  |  |  | Year
Number | Description |  |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital cost; RO-RO |  |  | 36000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; UF |  |  | 30000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; EDI Stacks |  |  | 10500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  |  | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Annualised Labour Cost |  |  | 192720 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440
8 | RO Membrane Replacement - Pass 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245552 | 0 | 0 | 0 | 0 | 0 | 0 | 1245552 | 0 | 0 | 0 | 0 | 0 | 0 | 1245552 | 0 | 0 | 0 | 0 | 0 | 0 | 1245552 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | RO Membrane Replacement - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201068 | 0 | 0 | 0 | 0 | 0 | 0 | 1201068 | 0 | 0 | 0 | 0 | 0 | 0 | 1201068 | 0 | 0 | 0 | 0 | 0 | 0 | 1201068 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | UF Membrane Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 0
11 | Power Costs - Pass 1 |  |  | 702447.8436 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872 | 1404895.6872
12 | Power Costs - Pass 2 |  |  | 523006.2691 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382 | 1046012.5382
13 | Power Costs - UF |  |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
14 | Power costs - GTM |  |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
15 | Dechlorination (SMBS) - Pass 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Dechlorination (SMBS) - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Antiscalant - Pass 1 |  |  | 32781.672 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344 | 65563.344
18 | Antiscalant - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Acid (H2SO4) - Pass 1 |  |  | 32367.9985 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997 | 64735.997
20 | Caustic (NaOH) - Pass 2 |  |  | 73911.9773 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546
21 | UF CEB NaOCl costs |  |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
22 | UF CEB HCl Costs |  |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
23 | UF Backwash water replacement |  |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
24 | Annualised EDI Stack Power Costs |  |  | 552798.3283 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566
25 | EDI Stack Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0
26 | GTM Contactor Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Annualised GTM N2 costs |  |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
28 | NR-MBIX Cation Resin Replacement |  |  | 0 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0
29 | NR-MBIX Anion Resin Replacement |  |  | 0 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0
30 | Raw Water |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | CIP |  |  | 30000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
| Total |  |  | 91386462.445 | 6172924.89 | 6332724.89 | 6172924.89 | 6332724.89 | 9499324.89 | 6332724.89 | 13038544.89 | 12632724.89 | 6172924.89 | 9659124.89 | 6172924.89 | 6332724.89 | 6172924.89 | 13198344.89 | 9499324.89 | 12632724.89 | 6172924.89 | 6332724.89 | 6172924.89 | 9659124.89 | 13038544.89 | 6332724.89 | 6172924.89 | 12632724.89 | 9499324.89 | 6332724.89 | 6172924.89 | 13198344.89 | 6172924.89 | 9659124.89 | 6172924.89 | 12632724.89 | 6172924.89 | 6332724.89 | 6172924.89
| discounted demin water |  |  | 2162962.963 | 2002743.4842 | 1854392.115 | 1717029.7361 | 1589842.3483 | 1472076.2484 | 1363033.5633 | 1262068.1142 | 1168581.5872 | 1082019.9882 | 1001870.3594 | 927657.7402 | 858942.352 | 795316.9926 | 736404.6228 | 681856.1322 | 631348.2706 | 584581.732 | 541279.3815 | 501184.6125 | 464059.8264 | 429685.0244 | 397856.5041 | 368385.6519 | 341097.8259 | 315831.3203 | 292436.4076 | 270774.4515 | 250717.0847 | 232145.4488 | 214949.4897 | 199027.3052 | 184284.5419 | 170633.8351 | 157994.2917 | 146291.0109 | 23399252.1702
| Index |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  |  | 105903407.6239 | 7700751.2521 | 8504460.3011 | 8924032.9151 | 9855412.955 | 15914426.0501 | 11420967.4775 | 25313688.6426 | 26402033.6331 | 13888181.0169 | 23394091.8839 | 16094349.8198 | 17774078.7404 | 18650973.501 | 42928332.5252 | 33260695.1774 | 47615642.9818 | 25047111.0732 | 27661218.3418 | 29025901.0231 | 48892982.7977 | 71048009.0259 | 37147316.1007 | 38980001.0647 | 85874046.2223 | 69513901.4251 | 49886562.35 | 52347745.6149 | 120487085.0621 | 60663302.7883 | 102184935.3555 | 70299804.9286 | 154872461.0819 | 81467087.1161 | 89969612.7752 | 94408317.2055
| Discount |  |  | 90795102.5582 | 6113104.624 | 6251032.2032 | 6073546.8518 | 6210581.9046 | 9285914.7463 | 6170393.359 | 12663146.5977 | 12229250.0511 | 5956402.7855 | 9290115.7581 | 5917859.0277 | 6051381.3572 | 5879564.6857 | 12530371.0524 | 8989333.2099 | 11915768.4269 | 5803717.8039 | 5934664.8098 | 5766162.0674 | 8993400.0462 | 12100561.8555 | 5858107.1318 | 5691778.089 | 11610322.5146 | 8702224.1499 | 5782537.0542 | 5618353.6701 | 11973685.1202 | 5581997.4211 | 8706161.096 | 5545876.4325 | 11312706.3286 | 5509989.1822 | 5634308.9045 | 5474334.1574
| Actual Net Present Value |  |  | 90795102.5582 | 96908207.1822 | 103159239.3854 | 109232786.2373 | 115443368.1419 | 124729282.8882 | 130899676.2472 | 143562822.845 | 155792072.896 | 161748475.6815 | 171038591.4397 | 176956450.4674 | 183007831.8246 | 188887396.5103 | 201417767.5627 | 210407100.7727 | 222322869.1996 | 228126587.0035 | 234061251.8133 | 239827413.8808 | 248820813.927 | 260921375.7825 | 266779482.9142 | 272471261.0032 | 284081583.5178 | 292783807.6677 | 298566344.7219 | 304184698.3921 | 316158383.5122 | 321740380.9333 | 330446542.0293 | 335992418.4619 | 347305124.7904 | 352815113.9726 | 358449422.8771 | 363923757.0345
| Actual Net Present Value ( x R 1000) |  |  | 90795.1026 | 96908.2072 | 103159.2394 | 109232.7862 | 115443.3681 | 124729.2829 | 130899.6762 | 143562.8228 | 155792.0729 | 161748.4757 | 171038.5914 | 176956.4505 | 183007.8318 | 188887.3965 | 201417.7676 | 210407.1008 | 222322.8692 | 228126.587 | 234061.2518 | 239827.4139 | 248820.8139 | 260921.3758 | 266779.4829 | 272471.261 | 284081.5835 | 292783.8077 | 298566.3447 | 304184.6984 | 316158.3835 | 321740.3809 | 330446.542 | 335992.4185 | 347305.1248 | 352815.114 | 358449.4229 | 363923.757
| avg FOM (undiscounted) | 4710234.9647 | FOM (net of Power) | 1327196.8835 | 2654393.767 | 2814193.767 | 2654393.767 | 2814193.767 | 5980793.767 | 2814193.767 | 9520013.767 | 9114193.767 | 2654393.767 | 6140593.767 | 2654393.767 | 2814193.767 | 2654393.767 | 9679813.767 | 5980793.767 | 9114193.767 | 2654393.767 | 2814193.767 | 2654393.767 | 6140593.767 | 9520013.767 | 2814193.767 | 2654393.767 | 9114193.767 | 5980793.767 | 2814193.767 | 2654393.767 | 9679813.767 | 2654393.767 | 6140593.767 | 2654393.767 | 9114193.767 | 2654393.767 | 2814193.767 | 2654393.767

## RO-Mix
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 3:
Membrane-based System: Double Pass Reverse Osmosis; Water Source - 50:50, Mokolo:Crocodile Configuration : Raw → UF → RO 1st Pass → RO 2nd Pass → EDI → GTM → NRMB
Results |  |  |  |  | 0.564 | R/kwh | 2.7434 | kWh/m3 | 0.80808 | System EFF
Net Present Value this Scenario |  |  | 316910654.9271 |  | 13.5436 | /m3 | 4.8859 | demin$:raw$
[5 empty] | 14.8963 | 2010ZAR
Manpower: |  |  |  |  | RO Plant Data: | [13 empty] | Chemical usage :
Number of Chemist/Operators for WTP per shift |  | 1 |  |  | Number of array stages in 1st Pass |  |  | 3 |  |  |  | Number of array stages in 2nd Pass |  |  | 3 |  |  |  | Pass 1 pH adjustment |  |  | acid |  |  | Pass 2 pH adjustment |  |  | caustic
Number of Shifts per day |  | 3 | [5 empty] | 1st Stage | 2nd Stage | 3rd Stage |  |  |  |  | 1st Stage | 2nd Stage | 3rd Stage |  | Pass 1 Dose rate (as 100% chemical) |  |  | 56.55 | mg/L |  | Pass 2 Dose rate (as 100% chemical) |  |  | 27.29 | mg/L
Duration of shift |  | 9 | hours |  | Number of pressure vessels 1st Pass |  |  | 48 | 24 | 12 |  | Number of pressure vessels 2nd Pass |  |  | 45 | 24 | 12 |  | Pass 1 pH adjustment Chemical usage (as 100% chemical) |  |  | 22.3938 | kg/h |  | Pass 2 pH adjustment Chemical usage (as 100% chemical) |  |  | 10.8068 | kg/h
Average time spent per shift on demin plant |  | 2 | hours |  | Number of membrane elements per pressure vessel |  |  | 7 | 7 | 7 |  | Number of membrane elements per pressure vessel |  |  | 7 | 7 | 7 |  |  |  |  | 176552.7192 | kg p a |  |  |  |  | 85201.1266 | kg p a
Fraction of shift time spent on demin plant (average) |  | 22.22% |  |  | Number of membrane elements per stage |  |  | 336 | 168 | 84 |  | Number of membrane elements per stage |  |  | 315 | 168 | 84 |  | Annualised pH adjustment Chemical cost - Pass 1 |  |  | 97103.9956 |  |  | Annualised pH adjustment Chemical cost - Pass 2 |  |  | 147823.9546
Number of days per annum |  | 365 | days |  | Total number of membrane elements in 1st Pass |  |  | 588 |  |  |  | Total number of membrane elements in 2nd Pass |  |  | 567 |  |  |  | Pass 1 Antiscalant |  |  | for BaSO4 |  |  | Pass 2 Antiscalant |  |  | nil
Plant availability |  | 90% |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Pass 1Antiscalant Dose rate (as 100% chemical) |  |  | 0.75 | mg/L |  | Pass 2Antiscalant Dose rate (as 100% chemical) |  |  | 0 | mg/L
Number of operating days |  | 328.5 | days |  | Membrane Replacement cost |  |  | 2179716 |  |  |  | Membrane Replacement cost |  |  | 2101869 |  |  |  | Pass 1 Antiscalant Chemical usage (as 100% chemical) |  |  | 0.297 | kg/h |  | Pass 2 Antiscalant Chemical usage (as 100% chemical) |  |  | 0 | kg/h
Number of manhours per annum on demin plant |  | 1752 | hours |  | Pass 1 Feed Flow |  |  | 396 | m3/h |  |  | Pass 2 Feed Flow |  |  | 369 | m3/h | [5 empty] | 2341.548 | kg p a |  |  |  |  | 0 | kg p a
Annualised Labour Cost |  | 385440 |  |  | Pass 1 Product (permeate) Flow |  |  | 352.95 | m3/h |  |  | Pass 2 Product (permeate) Flow |  |  | 335.4 | m3/h |  |  | Annualised Antiscalant cost - Pass 1 |  |  | 98345.016 |  |  | Annualised Antiscalant cost - Pass 2 |  |  | 0
[5 empty] | Pass 1 Reject (concentrate) Flow |  |  | 43.05 | m3/h |  |  | Pass 2 Reject (concentrate) Flow (recycled to Pass 1) |  |  | 33.6 | m3/h |  |  | Pass 1 Dechlorination |  |  | SMBS |  |  | Pass 2 Dechlorination |  |  | nil
[5 empty] | Pass 1 Recovery |  |  | 89.13% |  |  |  | Pass 2 Recovery |  |  | 90.89% |  |  |  | Pass 1 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L |  | Pass 2 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L
[5 empty] | Pass 1 Average flux |  |  | 25.7 | Lmh |  |  | Pass 2 Average flux |  |  | 25.32 | Lmh |  |  | Pass 1 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h |  | Pass 2 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h
20 yr | 316910654.9271 |  |  |  | Pass 1 power consumption |  |  | 473.925 | kW |  |  | Pass 2 power consumption |  |  | 352.86 | kW | [5 empty] | 0 | kg p a |  |  |  |  | 0 | kg p a
35yr | 455968484.5812 |  |  |  | Pass 1 Annualised power cost |  |  | 2107343.5308 |  |  |  | Pass 2 Annualised power cost |  |  | 1569018.8074 |  |  |  | Annualised Dechlorination cost - Pass 1 |  |  | 0 |  |  | Annualised Dechlorination cost - Pass 2 |  |  | 0
power cost | 3903582.3718
[5 empty] | RO Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | EDI Plant Data : |  |  |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data :
hours of operation | 7884 |  |  |  | Raw Water Usage for demin production |  | 3122064 | m3 per annum | raw water cost: | Flow to UF plant |  | 255.5 | m3/h |  | EDI Feed flow |  | 336 | m3/h |  | Cation Resin Volume |  | 2.5 | m3 |  | Flow through GTM |  | 320 | m3/h
power |  |  |  |  | Annualised Raw Water cost |  | 0 |  | 0 | Number of UF pressure vessels housings |  | 36 |  |  | EDI Demin production flow |  | 320 | m3/h |  | Anion Resin Volume |  | 2.5 | m3 |  | Number of Skids (parallel operation) |  | 6
UF plant |  |  |  |  | Average equivalent weight of influent stream |  | 26 | g/equiv | 8654361.408 | Number of UF elements per housing |  | 4 |  |  | EDI Concentrate flow (recycled to 2nd Pass RO) |  | 16 | m3/h |  | Resin Replacement Frequency |  | 2 | years |  | GTM Contactors per skid (series operation) |  | 4
[5 empty] | TDS of RO influent stream |  | 453.9 | mg/L (as ions) |  | Total number of UF elements |  | 144 |  |  | EDI Recovery |  | 95.24% |  |  | Cation Resin Replacement Cost |  | 53150 |  |  | Total number of contactors |  | 24
[7 empty] | 17.4577 | meq/L |  | UF Element replacement Cost |  | 4989600 |  |  | EDI power requirement |  | 0.74 | kWh/m3 |  | Anion Resin Replacement Cost |  | 106650 |  |  | Frequency of GTM replacement |  | 7 | years
[5 empty] | Cleaning-in-place (CIP) Frequency |  | 4 | per annum |  | UF element replacement frequency |  | 5 | years |  |  |  | 1960277.76 | kWh p a | [6 empty] | Cost of GTM Replacement |  | 4419000
[5 empty] | Annualised CIP costs |  | 60000 |  |  | UF system Recovery |  | 92.9 | % |  | Annualised EDI power cost |  | 1105596.6566 | [7 empty] | Nitrogen sweep rate |  | 7.5 | Nm3/h
[5 empty] | Volume of effluent produced |  | 339406.2 | m3 per annum |  | UF System Backwash water |  | 18.1405 | m3/h |  | EDI Stack replacement frequency |  | 8 | years | [6 empty] | Nitrogen usage per annum |  | 59130 | Nm3
[5 empty] | Average equivalent weight of influent stream |  | 26 | g/equiv |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | EDI Stack replacement costs (60% of new) |  | 6300000 | [7 empty] | Annualised usage @ 1.1455 kg/m3 @ NTP |  | 51619.3802 | kg
[5 empty] | TDS of RO reject stream |  | 4175.2474 | mg/L (as ions) |  | UF Power Requirement |  | 0.2 | kWh/m3 | [11 empty] | Annualised N2 costs |  | 412955.0415
[7 empty] | 160.5864 | meq/L |  | Annualised UF Power Usage |  | 402872.4 | kWh | [11 empty] | Power requirement for GTM |  | 189 | kW
[5 empty] | Effluent solids loading per annum |  | 54504032.6769 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 | [12 empty] | Annualised GTM power usage |  | 1490076 | kWh
[7 empty] | 2725.2016 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d | [11 empty] | Annualised GTM power costs |  | 840402.864
[12 empty] | 1090.62 | L per annum | 7884
[10 empty] | Annualised CEB NaOCl cost |  | 14897.8692
[10 empty] | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[12 empty] | 1304.145 | L per annum
[10 empty] | Annualised CEB HCl cost |  | 930.2901
Events/Activities |  |  | Year
Number | Description |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital cost; RO-RO |  | 54000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; UF |  | 45000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; EDI Stacks |  | 10500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Annualised Labour Cost |  | 192720 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440
8 | RO Membrane Replacement - Pass 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2179716 | 0 | 0 | 0 | 0 | 0 | 0 | 2179716 | 0 | 0 | 0 | 0 | 0 | 0 | 2179716 | 0 | 0 | 0 | 0 | 0 | 0 | 2179716 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | RO Membrane Replacement - Pass 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2101869 | 0 | 0 | 0 | 0 | 0 | 0 | 2101869 | 0 | 0 | 0 | 0 | 0 | 0 | 2101869 | 0 | 0 | 0 | 0 | 0 | 0 | 2101869 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | UF Membrane Replacement |  | 0 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 0
11 | GTM Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Power Costs - Pass 1 |  | 1053671.7654 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308
13 | Power Costs - Pass 2 |  | 784509.4037 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074
14 | Power Costs - UF |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
15 | GTM Power Costs |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
16 | Dechlorination (SMBS) - Pass 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Dechlorination (SMBS) - Pass 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Antiscalant - Pass 1 |  | 49172.508 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016 | 98345.016
19 | Antiscalant - Pass 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Acid (H2SO4) - Pass 1 |  | 48551.9978 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956 | 97103.9956
21 | Caustic (NaOH) - Pass 2 |  | 73911.9773 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546
22 | UF CEB NaOCl costs |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
23 | UF CEB HCl Costs |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
24 | UF Backwash water replacement |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
25 | GTM N2 Costs |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
26 | Annualised EDI Stack Power Costs |  | 552798.3283 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566
27 | EDI Stack Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0
28 | NR-MBIX Cation Resin Replacement |  | 0 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0
29 | NR-MBIX Anion Resin Replacement |  | 0 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0
30 | Raw Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | CIP |  | 30000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
| Total |  | 125031764.3366 | 7463528.6733 | 7623328.6733 | 7463528.6733 | 7623328.6733 | 12453128.6733 | 7623328.6733 | 16164113.6733 | 13923328.6733 | 7463528.6733 | 12612928.6733 | 7463528.6733 | 7623328.6733 | 7463528.6733 | 16323913.6733 | 12453128.6733 | 13923328.6733 | 7463528.6733 | 7623328.6733 | 7463528.6733 | 12612928.6733 | 16164113.6733 | 7623328.6733 | 7463528.6733 | 13923328.6733 | 12453128.6733 | 7623328.6733 | 7463528.6733 | 16323913.6733 | 7463528.6733 | 12612928.6733 | 7463528.6733 | 13923328.6733 | 7463528.6733 | 7623328.6733 | 7463528.6733
| discounted demin water |  | 2162962.963 | 2002743.4842 | 1854392.115 | 1717029.7361 | 1589842.3483 | 1472076.2484 | 1363033.5633 | 1262068.1142 | 1168581.5872 | 1082019.9882 | 1001870.3594 | 927657.7402 | 858942.352 | 795316.9926 | 736404.6228 | 681856.1322 | 631348.2706 | 584581.732 | 541279.3815 | 501184.6125 | 464059.8264 | 429685.0244 | 397856.5041 | 368385.6519 | 341097.8259 | 315831.3203 | 292436.4076 | 270774.4515 | 250717.0847 | 232145.4488 | 214949.4897 | 199027.3052 | 184284.5419 | 170633.8351 | 157994.2917 | 146291.0109 | 23399252.1702
| Index |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  | 144893341.423 | 9310785.2111 | 10237661.858 | 10789824.3912 | 11863937.4789 | 20862997.9138 | 13748550.6413 | 31381825.515 | 29099358.6195 | 16791851.3647 | 30548110.2758 | 19459274.7357 | 21396420.4124 | 22550424.3108 | 53094414.498 | 43603068.8077 | 52480225.2084 | 30283833.8401 | 33298550.4004 | 35094488.9842 | 63844676.5802 | 88079467.7504 | 44717906.57 | 47129741.7048 | 94647242.0214 | 91129166.4459 | 60053400.0415 | 63292346.3898 | 149020259.1072 | 73346478.0217 | 133433547.6345 | 84997731.085 | 170694778.5892 | 98499811.9127 | 108305341.0187 | 114146728.6596
| Discount |  | 124222686.4052 | 7391201.4898 | 7524987.0885 | 7343373.1796 | 7476293.0545 | 12173358.8991 | 7427914.1185 | 15698725.8006 | 13478633.42 | 7201737.2269 | 12131074.8911 | 7155134.9359 | 7284647.575 | 7108834.2074 | 15497753.4727 | 11784555.6865 | 13133125.4062 | 7017129.6448 | 7144144.2976 | 6971721.9457 | 11743622.1816 | 15001279.5901 | 7051984.2318 | 6881786.1428 | 12796474.0609 | 11408170.4054 | 6961013.0387 | 6793010.5194 | 14809235.846 | 6749053.0905 | 11368544.27 | 6705380.1091 | 12468452.3543 | 6661989.7347 | 6782576.122 | 6618880.1385
| Actual Net Present Value |  | 124222686.4052 | 131613887.895 | 139138874.9835 | 146482248.163 | 153958541.2175 | 166131900.1166 | 173559814.2351 | 189258540.0357 | 202737173.4557 | 209938910.6825 | 222069985.5737 | 229225120.5096 | 236509768.0847 | 243618602.2921 | 259116355.7648 | 270900911.4512 | 284034036.8575 | 291051166.5023 | 298195310.7998 | 305167032.7455 | 316910654.9271 | 331911934.5171 | 338963918.7489 | 345845704.8918 | 358642178.9526 | 370050349.3581 | 377011362.3967 | 383804372.9162 | 398613608.7621 | 405362661.8526 | 416731206.1227 | 423436586.2318 | 435905038.5861 | 442567028.3208 | 449349604.4428 | 455968484.5812
| Actual Net Present Value ( x R 1000) |  | 124222.6864 | 131613.8879 | 139138.875 | 146482.2482 | 153958.5412 | 166131.9001 | 173559.8142 | 189258.54 | 202737.1735 | 209938.9107 | 222069.9856 | 229225.1205 | 236509.7681 | 243618.6023 | 259116.3558 | 270900.9115 | 284034.0369 | 291051.1665 | 298195.3108 | 305167.0327 | 316910.6549 | 331911.9345 | 338963.9187 | 345845.7049 | 358642.179 | 370050.3494 | 377011.3624 | 383804.3729 | 398613.6088 | 405362.6619 | 416731.2061 | 423436.5862 | 435905.0386 | 442567.0283 | 449349.6044 | 455968.4846

## RO-Croc
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 3:
Membrane-based System: Double Pass Reverse Osmosis; Water Source - Crocodile West System Only Configuration : Raw → UF → RO 1st Pass → RO 2nd Pass → EDI → GTM → NRMB
Results | [5 empty] | 0.564 | R/kwh | 2.7434 | kWh/m3 | 0.80808 | System EFF
Net Present Value this Scenario |  |  |  | 360069918.5773 |  | 15.3881 | /m3 | 5.5513 | demin$:raw$
[6 empty] | 16.925 | 2010ZAR
Manpower: | [5 empty] | RO Plant Data: | [13 empty] | Chemical usage :
Number of Chemist/Operators for WTP per shift |  |  | 1 |  |  | Number of array stages in 1st Pass |  |  | 3 |  |  |  | Number of array stages in 2nd Pass |  |  | 3 |  |  |  | Pass 1 pH adjustment |  |  | acid |  |  | Pass 2 pH adjustment |  |  | caustic
Number of Shifts per day |  |  | 3 | [5 empty] | 1st Stage | 2nd Stage | 3rd Stage |  |  |  |  | 1st Stage | 2nd Stage | 3rd Stage |  | Pass 1 Dose rate (as 100% chemical) |  |  | 75.4 | mg/L |  | Pass 2 Dose rate (as 100% chemical) |  |  | 27.29 | mg/L
Duration of shift |  |  | 9 | hours |  | Number of pressure vessels 1st Pass |  |  | 64 | 32 | 16 |  | Number of pressure vessels 2nd Pass |  |  | 60 | 32 | 16 |  | Pass 1 pH adjustment Chemical usage (as 100% chemical) |  |  | 29.8584 | kg/h |  | Pass 2 pH adjustment Chemical usage (as 100% chemical) |  |  | 10.8068 | kg/h
Average time spent per shift on demin plant |  |  | 2 | hours |  | Number of membrane elements per pressure vessel |  |  | 7 | 7 | 7 |  | Number of membrane elements per pressure vessel |  |  | 7 | 7 | 7 |  |  |  |  | 235403.6256 | kg p a |  |  |  |  | 85201.1266 | kg p a
Fraction of shift time spent on demin plant (average) |  |  | 22.22% |  |  | Number of membrane elements per stage |  |  | 448 | 224 | 112 |  | Number of membrane elements per stage |  |  | 420 | 224 | 112 |  | Annualised pH adjustment Chemical cost - Pass 1 |  |  | 129471.9941 |  |  | Annualised pH adjustment Chemical cost - Pass 2 |  |  | 147823.9546
Number of days per annum |  |  | 365 | days |  | Total number of membrane elements in 1st Pass |  |  | 784 |  |  |  | Total number of membrane elements in 2nd Pass |  |  | 756 |  |  |  | Pass 1 Antiscalant |  |  | for BaSO4 |  |  | Pass 2 Antiscalant |  |  | nil
Plant availability |  |  | 90% |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF) |  |  | Pass 1Antiscalant Dose rate (as 100% chemical) |  |  | 1 | mg/L |  | Pass 2Antiscalant Dose rate (as 100% chemical) |  |  | 0 | mg/L
Number of operating days |  |  | 328.5 | days |  | Membrane Replacement cost |  |  | 2906288 |  |  |  | Membrane Replacement cost |  |  | 2802492 |  |  |  | Pass 1 Antiscalant Chemical usage (as 100% chemical) |  |  | 0.396 | kg/h |  | Pass 2 Antiscalant Chemical usage (as 100% chemical) |  |  | 0 | kg/h
Number of manhours per annum on demin plant |  |  | 1752 | hours |  | Pass 1 Feed Flow |  |  | 396 | m3/h |  |  | Pass 2 Feed Flow |  |  | 369 | m3/h | [5 empty] | 3122.064 | kg p a |  |  |  |  | 0 | kg p a
Annualised Labour Cost |  |  | 385440 |  |  | Pass 1 Product (permeate) Flow |  |  | 352.95 | m3/h |  |  | Pass 2 Product (permeate) Flow |  |  | 335.4 | m3/h |  |  | Annualised Antiscalant cost - Pass 1 |  |  | 131126.688 |  |  | Annualised Antiscalant cost - Pass 2 |  |  | 0
[6 empty] | Pass 1 Reject (concentrate) Flow |  |  | 43.05 | m3/h |  |  | Pass 2 Reject (concentrate) Flow (recycled to Pass 1) |  |  | 33.6 | m3/h |  |  | Pass 1 Dechlorination |  |  | SMBS |  |  | Pass 2 Dechlorination |  |  | nil
[6 empty] | Pass 1 Recovery |  |  | 89.13% |  |  |  | Pass 2 Recovery |  |  | 90.89% |  |  |  | Pass 1 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L |  | Pass 2 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L
[6 empty] | Pass 1 Average flux |  |  | 25.7 | Lmh |  |  | Pass 2 Average flux |  |  | 25.32 | Lmh |  |  | Pass 1 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h |  | Pass 2 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h
20 yr | 360069918.5773 |  |  |  |  | Pass 1 power consumption |  |  | 473.925 | kW |  |  | Pass 2 power consumption |  |  | 352.86 | kW | [5 empty] | 0 | kg p a |  |  |  |  | 0 | kg p a
35yr | 505656442.1763 |  |  |  |  | Pass 1 Annualised power cost |  |  | 2107343.5308 |  |  |  | Pass 2 Annualised power cost |  |  | 1569018.8074 |  |  |  | Annualised Dechlorination cost - Pass 1 |  |  | 0 |  |  | Annualised Dechlorination cost - Pass 2 |  |  | 0
power cost | 3903582.3718 | /annum
[6 empty] | RO Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | EDI Plant Data : |  |  |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data :
[6 empty] | Raw Water Usage for demin production |  | 3122064 | m3 per annum | raw water cost: | Flow to UF plant |  | 255.5 | m3/h |  | EDI Feed flow |  | 336 | m3/h |  | Cation Resin Volume |  | 2.5 | m3 |  | Flow through GTM |  | 320 | m3/h
[6 empty] | Annualised Raw Water cost |  | 0 |  | 0 | Number of UF pressure vessels housings |  | 48 |  |  | EDI Demin production flow |  | 320 | m3/h |  | Anion Resin Volume |  | 2.5 | m3 |  | Number of Skids (parallel operation) |  | 6
[6 empty] | Average equivalent weight of influent stream |  | 26 | g/equiv | 8654361.408 | Number of UF elements per housing |  | 4 |  |  | EDI Concentrate flow (recycled to 2nd Pass RO) |  | 16 | m3/h |  | Resin Replacement Frequency |  | 2 | years |  | GTM Contactors per skid (series operation) |  | 4
[6 empty] | TDS of RO influent stream |  | 947 | mg/L (as ions) |  | Total number of UF elements |  | 192 |  |  | EDI Recovery |  | 95.24% |  |  | Cation Resin Replacement Cost |  | 53150 |  |  | Total number of contactors |  | 24
[8 empty] | 36.4231 | meq/L |  | UF Element replacement Cost |  | 6652800 |  |  | EDI power requirement |  | 0.74 | kWh/m3 |  | Anion Resin Replacement Cost |  | 106650 |  |  | Frequency of GTM replacement |  | 7 | years
[6 empty] | Cleaning-in-place (CIP) Frequency |  | 4 | per annum |  | UF element replacement frequency |  | 5 | years |  |  |  | 1960277.76 | kWh p a | [6 empty] | Cost of GTM Replacement |  | 4419000
[6 empty] | Annualised CIP costs |  | 60000 |  |  | UF system Recovery |  | 92.9 | % |  | Annualised EDI power cost |  | 1105596.6566 | [7 empty] | Nitrogen sweep rate |  | 7.5 | Nm3/h
[6 empty] | Volume of effluent produced |  | 339406.2 | m3 per annum |  | UF System Backwash water |  | 18.1405 | m3/h |  | EDI Stack replacement frequency |  | 8 | years | [6 empty] | Nitrogen usage per annum |  | 59130 | Nm3
[6 empty] | Average equivalent weight of influent stream |  | 26 | g/equiv |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | EDI Stack replacement costs (60% of new) |  | 6300000 | [7 empty] | Annualised usage @ 1.1455 kg/m3 @ NTP |  | 51619.3802 | kg
[6 empty] | TDS of RO reject stream |  | 8711.0801 | mg/L (as ions) |  | UF Power Requirement |  | 0.2 | kWh/m3 | [11 empty] | Annualised N2 costs |  | 412955.0415
[8 empty] | 335.0415 | meq/L |  | Annualised UF Power Usage |  | 402872.4 | kWh | [11 empty] | Power requirement for GTM |  | 189 | kW
[6 empty] | Effluent solids loading per annum |  | 113715177.2308 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 | [12 empty] | Annualised GTM power usage |  | 1490076 | kWh
[8 empty] | 5685.7589 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d | [11 empty] | Annualised GTM power costs |  | 840402.864
[13 empty] | 1090.62 | L per annum
[11 empty] | Annualised CEB NaOCl cost |  | 14897.8692
[11 empty] | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[13 empty] | 1304.145 | L per annum
[11 empty] | Annualised CEB HCl cost |  | 930.2901
Events/Activities |  |  |  | Year
Number | Description |  |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital cost; RO-RO |  |  | 72000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; UF |  |  | 60000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; EDI Stacks |  |  | 10500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  |  | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Annualised Labour Cost |  |  | 192720 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440 | 385440
8 | RO Membrane Replacement - Pass 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2906288 | 0 | 0 | 0 | 0 | 0 | 0 | 2906288 | 0 | 0 | 0 | 0 | 0 | 0 | 2906288 | 0 | 0 | 0 | 0 | 0 | 0 | 2906288 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | RO Membrane Replacement - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2802492 | 0 | 0 | 0 | 0 | 0 | 0 | 2802492 | 0 | 0 | 0 | 0 | 0 | 0 | 2802492 | 0 | 0 | 0 | 0 | 0 | 0 | 2802492 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | UF Membrane Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 0
11 | GTM Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Power Costs - Pass 1 |  |  | 1053671.7654 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308 | 2107343.5308
13 | Power Costs - Pass 2 |  |  | 784509.4037 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074 | 1569018.8074
14 | Power Costs - UF |  |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
15 | GTM Power Costs |  |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
16 | Dechlorination (SMBS) - Pass 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Dechlorination (SMBS) - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Antiscalant - Pass 1 |  |  | 65563.344 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688 | 131126.688
19 | Antiscalant - Pass 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Acid (H2SO4) - Pass 1 |  |  | 64735.997 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941 | 129471.9941
21 | Caustic (NaOH) - Pass 2 |  |  | 73911.9773 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546 | 147823.9546
22 | UF CEB NaOCl costs |  |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
23 | UF CEB HCl Costs |  |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
24 | UF Backwash water replacement |  |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
25 | GTM N2 Costs |  |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
26 | Annualised EDI Stack Power Costs |  |  | 552798.3283 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566 | 1105596.6566
27 | EDI Stack Replacement |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300000 | 0 | 0 | 0
28 | NR-MBIX Cation Resin Replacement |  |  | 0 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0 | 53150 | 0
29 | NR-MBIX Anion Resin Replacement |  |  | 0 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0 | 106650 | 0
30 | Raw Water |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | CIP |  |  | 30000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000
| Total |  |  | 158064339.1719 | 7528678.3438 | 7688478.3438 | 7528678.3438 | 7688478.3438 | 14181478.3438 | 7688478.3438 | 17656458.3438 | 13988478.3438 | 7528678.3438 | 14341278.3438 | 7528678.3438 | 7688478.3438 | 7528678.3438 | 17816258.3438 | 14181478.3438 | 13988478.3438 | 7528678.3438 | 7688478.3438 | 7528678.3438 | 14341278.3438 | 17656458.3438 | 7688478.3438 | 7528678.3438 | 13988478.3438 | 14181478.3438 | 7688478.3438 | 7528678.3438 | 17816258.3438 | 7528678.3438 | 14341278.3438 | 7528678.3438 | 13988478.3438 | 7528678.3438 | 7688478.3438 | 7528678.3438
| discounted demin water |  |  | 2162962.963 | 2002743.4842 | 1854392.115 | 1717029.7361 | 1589842.3483 | 1472076.2484 | 1363033.5633 | 1262068.1142 | 1168581.5872 | 1082019.9882 | 1001870.3594 | 927657.7402 | 858942.352 | 795316.9926 | 736404.6228 | 681856.1322 | 631348.2706 | 584581.732 | 541279.3815 | 501184.6125 | 464059.8264 | 429685.0244 | 397856.5041 | 368385.6519 | 341097.8259 | 315831.3203 | 292436.4076 | 270774.4515 | 250717.0847 | 232145.4488 | 214949.4897 | 199027.3052 | 184284.5419 | 170633.8351 | 157994.2917 | 146291.0109 | 23399252.1702
| Index |  |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  |  | 183173215.0941 | 9392059.7148 | 10325153.8613 | 10884009.5327 | 11965327.7837 | 23758539.7906 | 13866047.0242 | 34279138.7241 | 29235519.5671 | 16938428.6248 | 34734117.9587 | 19629136.1234 | 21579276.1962 | 22747268.5621 | 57948346.4714 | 49654668.4968 | 52725789.2874 | 30548183.5711 | 33583122.8858 | 35400831.2648 | 72593312.8875 | 96211365.7893 | 45100069.9272 | 47541140.559 | 95090112.8879 | 103776836.6768 | 60566621.9416 | 63844829.7652 | 162643805.147 | 73986724.6243 | 151717947.2427 | 85739682.301 | 171493489.0732 | 99359623.7488 | 109230928.4603 | 115143123.5405
| Discount |  |  | 157041508.1397 | 7455719.8112 | 7589296.3228 | 7407474.0043 | 7540186.145 | 13862879.7733 | 7491393.7582 | 17148103.7409 | 13541702.2843 | 7264601.7013 | 13793396.1358 | 7217592.6157 | 7346902.8456 | 7170887.7248 | 16914569.9459 | 13420115.189 | 13194577.5785 | 7078382.6666 | 7205198.8142 | 7032578.6004 | 13352850.7798 | 16386266.1164 | 7112251.14 | 6941857.7416 | 12856350.9832 | 12991492.0011 | 7020502.4986 | 6852307.1895 | 16163107.5113 | 6807966.053 | 12926375.9404 | 6763911.8471 | 12526794.4061 | 6720142.715 | 6840540.6436 | 6676656.8121
| Actual Net Present Value |  |  | 157041508.1397 | 164497227.9509 | 172086524.2736 | 179493998.2779 | 187034184.4229 | 200897064.1962 | 208388457.9544 | 225536561.6953 | 239078263.9796 | 246342865.6809 | 260136261.8167 | 267353854.4324 | 274700757.278 | 281871645.0028 | 298786214.9488 | 312206330.1378 | 325400907.7163 | 332479290.3829 | 339684489.1971 | 346717067.7975 | 360069918.5773 | 376456184.6937 | 383568435.8336 | 390510293.5752 | 403366644.5584 | 416358136.5595 | 423378639.0581 | 430230946.2476 | 446394053.7589 | 453202019.8119 | 466128395.7523 | 472892307.5994 | 485419102.0055 | 492139244.7206 | 498979785.3641 | 505656442.1763
| Actual Net Present Value ( x R 1000) |  |  | 157041.5081 | 164497.228 | 172086.5243 | 179493.9983 | 187034.1844 | 200897.0642 | 208388.458 | 225536.5617 | 239078.264 | 246342.8657 | 260136.2618 | 267353.8544 | 274700.7573 | 281871.645 | 298786.2149 | 312206.3301 | 325400.9077 | 332479.2904 | 339684.4892 | 346717.0678 | 360069.9186 | 376456.1847 | 383568.4358 | 390510.2936 | 403366.6446 | 416358.1366 | 423378.6391 | 430230.9462 | 446394.0538 | 453202.0198 | 466128.3958 | 472892.3076 | 485419.102 | 492139.2447 | 498979.7854 | 505656.4422
| avg FOM (undiscounted) | 5755586.8148 | FOM (net of Power) | 1392346.554 | 2784693.108 | 2944493.108 | 2784693.108 | 2944493.108 | 9437493.108 | 2944493.108 | 12912473.108 | 9244493.108 | 2784693.108 | 9597293.108 | 2784693.108 | 2944493.108 | 2784693.108 | 13072273.108 | 9437493.108 | 9244493.108 | 2784693.108 | 2944493.108 | 2784693.108 | 9597293.108 | 12912473.108 | 2944493.108 | 2784693.108 | 9244493.108 | 9437493.108 | 2944493.108 | 2784693.108 | 13072273.108 | 2784693.108 | 9597293.108 | 2784693.108 | 9244493.108 | 2784693.108 | 2944493.108 | 2784693.108

## RO-Mo-DataSummary
Scenario 1:
Membrane-based System: Double Pass Reverse Osmosis; Water Source - Mokolo System Only Configuration : Raw → UF → RO 1st Pass → RO 2nd Pass → EDI → GTM → NRMB
Results
NPV this Scenario |  |  | 248820813.927
Manpower:
Number of Chemist/Operators for WTP per shift |  | 1
Number of Shifts per day |  | 3
Duration of shift |  | 9 | hours
Average time spent per shift on demin plant |  | 2 | hours
Fraction of shift time spent on demin plant (average) |  | 22.22%
Number of days per annum |  | 365 | days
Plant availability |  | 90%
Number of operating days |  | 328.5 | days
Number of manhours per annum on demin plant |  | 1752 | hours
Annualised Labour Cost |  | 385440
RO Plant Data:
Number of array stages in 1st Pass |  | 3 |  |  |  | Number of array stages in 2nd Pass |  |  | 3
|  | 1st Stage | 2nd Stage | 3rd Stage |  |  |  |  | 1st Stage | 2nd Stage | 3rd Stage
Number of pressure vessels 1st Pass |  | 32 | 16 | 8 |  | Number of pressure vessels 2nd Pass |  |  | 30 | 16 | 8
Number of membrane elements per pressure vessel |  | 6 | 6 | 6 |  | Number of membrane elements per pressure vessel |  |  | 6 | 6 | 6
Number of membrane elements per stage |  | 192 | 96 | 48 |  | Number of membrane elements per stage |  |  | 180 | 96 | 48
Total number of membrane elements in 1st Pass |  | 336 |  |  |  | Total number of membrane elements in 2nd Pass |  |  | 324
Membrane replacement frequency |  | 7 | years (preceded by UF) |  |  | Membrane replacement frequency |  |  | 7 | years (preceded by UF)
Membrane Replacement cost |  | 1245552 |  |  |  | Membrane Replacement cost |  |  | 1201068
Pass 1 Feed Flow |  | 396 | m3/h |  |  | Pass 2 Feed Flow |  |  | 369 | m3/h
Pass 1 Product (permeate) Flow |  | 352.95 | m3/h |  |  | Pass 2 Product (permeate) Flow |  |  | 335.4 | m3/h
Pass 1 Reject (concentrate) Flow |  | 43.05 | m3/h |  |  | Pass 2 Reject (concentrate) Flow (recycled to Pass 1) |  |  | 33.6 | m3/h
Pass 1 Recovery |  | 89.13% |  |  |  | Pass 2 Recovery |  |  | 90.89%
Pass 1 Average flux |  | 25.7 | Lmh |  |  | Pass 2 Average flux |  |  | 25.32 | Lmh
Pass 1 power consumption |  | 315.95 | kW |  |  | Pass 2 power consumption |  |  | 235.24 | kW
Pass 1 Annualised power cost |  | 1404895.6872 |  |  |  | Pass 2 Annualised power cost |  |  | 1046012.5382
Chemical usage :
Pass 1 pH adjustment |  | acid |  |  | Pass 2 pH adjustment |  |  | caustic
Pass 1 Dose rate (as 100% chemical) |  | 37.7 | mg/L |  | Pass 2 Dose rate (as 100% chemical) |  |  | 27.29 | mg/L
Pass 1 pH adjustment Chemical usage (as 100% chemical) |  | 14.9292 | kg/h |  | Pass 2 pH adjustment Chemical usage (as 100% chemical) |  |  | 10.8068 | kg/h
|  | 117701.8128 | kg p a |  |  |  |  | 85201.1266 | kg p a
Annualised pH adjustment Chemical cost - Pass 1 |  | 64735.997 |  |  | Annualised pH adjustment Chemical cost - Pass 2 |  |  | 147823.9546
Pass 1 Antiscalant |  | for BaSO4 |  |  | Pass 2 Antiscalant |  |  | nil
Pass 1Antiscalant Dose rate (as 100% chemical) |  | 0.5 | mg/L |  | Pass 2Antiscalant Dose rate (as 100% chemical) |  |  | 0 | mg/L
Pass 1 Antiscalant Chemical usage (as 100% chemical) |  | 0.198 | kg/h |  | Pass 2 Antiscalant Chemical usage (as 100% chemical) |  |  | 0 | kg/h
|  | 1561.032 | kg p a |  |  |  |  | 0 | kg p a
Annualised Antiscalant cost - Pass 1 |  | 65563.344 |  |  | Annualised Antiscalant cost - Pass 2 |  |  | 0
Pass 1 Dechlorination |  | SMBS |  |  | Pass 2 Dechlorination |  |  | nil
Pass 1 Dechlorination Dose rate (as 100% chemical) |  | 0 | mg/L |  | Pass 2 Dechlorination Dose rate (as 100% chemical) |  |  | 0 | mg/L
Pass 1 Dechlorination Chemical usage (as 100% chemical) |  | 0 | kg/h |  | Pass 2 Dechlorination Chemical usage (as 100% chemical) |  |  | 0 | kg/h
|  | 0 | kg p a |  |  |  |  | 0 | kg p a
Annualised Dechlorination cost - Pass 1 |  | 0 |  |  | Annualised Dechlorination cost - Pass 2 |  |  | 0
Scenario 1:
Mokolo Water Supply Only : Membrane-based System: Double Pass Reverse Osmosis; Configuration : Raw → UF → RO 1st Pass → RO 2nd Pass → EDI → GTM → NRMB
RO Miscellaneous : |  |  |  |  | UF Plant Data :
Raw Water Usage for demin production | 3122064 | m3 per annum |  |  | Flow to UF plant |  | 255.5 | m3/h
Annualised Raw Water cost | 8654361.408 |  |  |  | Number of UF pressure vessels housings |  | 24
Average equivalent weight of influent stream | 26 | g/equiv |  |  | Number of UF elements per housing |  | 4
TDS of RO influent stream | 92.8 | mg/L (as ions) |  |  | Total number of UF elements |  | 96
| 3.5692 | meq/L |  |  | UF Element replacement Cost |  | 3326400
Cleaning-in-place (CIP) Frequency | 4 | per annum |  |  | UF element replacement frequency |  | 5 | years
Annualised CIP costs | 60000 |  |  |  | UF system Recovery |  | 92.9 | %
Volume of effluent produced | 339406.2 | m3 per annum |  |  | UF System Backwash water |  | 18.1405 | m3/h
Average equivalent weight of influent stream | 26 | g/equiv |  |  | Annualised Backwash replacement water cost |  | 396450.6139
TDS of RO reject stream | 841 | mg/L (as ions) |  |  | UF Power Requirement |  | 0.2 | kWh/m3
| 32.3462 | meq/L |  |  | Annualised UF Power Usage |  | 402872.4 | kWh
Effluent solids loading per annum | 10978485.1615 | equivalents |  |  | Annualised UF Power Cost |  | 227220.0336
| 548.9243 | tonnes as CaCO3 |  |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d
[7 empty] | 1090.62 | L per annum
[5 empty] | Annualised CEB NaOCl cost |  | 14897.8692
[5 empty] | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[7 empty] | 1304.145 | L per annum
[5 empty] | Annualised CEB HCl cost |  | 930.2901
EDI Plant Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data :
EDI Feed flow | 336 | m3/h |  |  | Flow through GTM |  | 320 | m3/h
EDI Demin production flow | 320 | m3/h |  |  | Number of Skids (parallel operation) |  | 6
EDI Concentrate flow (recycled to 2nd Pass RO) | 16 | m3/h |  |  | GTM Contactors per skid (series operation) |  | 4
EDI Recovery | 95.24% |  |  |  | Total number of contactors |  | 24
EDI power requirement | 0.74 | kWh/m3 |  |  | Frequency of GTM replacement |  | 7 | years
| 1960277.76 | kWh p a |  |  | Cost of GTM Replacement |  | 4419000
Annualised EDI power cost | 1105596.6566 |  |  |  | Nitrogen sweep rate |  | 7.5 | Nm3/h
EDI Stack replacement frequency | 8 | years |  |  | Nitrogen usage per annum |  | 69379200 | Nm3
EDI Stack replacement costs (60% of new) | 6300000 |  |  |  | Annualised usage @ 1.1455 kg/m3 @ NTP |  | 60566739.4151 | kg
[5 empty] | Annualised N2 costs |  | 484533915.3208
[5 empty] | Power requirement for GTM |  | 189 | kW
[5 empty] | Annualised GTM power usage |  | 1748355840 | kWh
[5 empty] | Annualised GTM power costs |  | 986072693.76
Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
[5 empty] | Cation Resin Volume |  | 2.5 | m3
[5 empty] | Anion Resin Volume |  | 2.5 | m3
[5 empty] | Resin Replacement Frequency |  | 2 | years
[5 empty] | Cation Resin Replacement Cost |  | 53150
[5 empty] | Anion Resin Replacement Cost |  | 106650

## IX-Mo
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 2:
Ion Exchange-Based System: Conventional Primary Exchangers and Polishing Mixed Beds Configuration : Raw → UF → Cation (SAC) → Vacuum Degasser → Anion (SBA) → MBIX → GTM → NRMB?
Results
Net Present Value this Scenario |  |  | 586729735.6281
Manpower: |  |  |  |  | IX Cation Data : SAC - Amberjet 1500 H | [5 empty] | IX Anion Data : SBA - Amberjet 4200 Cl | [5 empty] | Mixed Bed (regenerable) Data : SAC/SBA - Amberjet 1500 H/ Ambersep 900 OH | [5 empty] | Chemical usage : | [5 empty] | IX Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data : |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
Number of Chemist/Operators for WTP per shift |  | 1 |  |  | Number of Trains |  |  | 3 |  |  | Number of Trains |  |  | 3 |  |  | Number of Trains |  |  | 3 |  |  | SAC Cation Regeneration |  |  | 840 | kg as 100% H2SO4 |  | Raw Water Usage for demin production |  | 2680560 | m3 per annum |  | Flow to UF plant |  | 255.5 | m3/h |  | Flow through GTM | 320 | m3/h | Cation Resin Volume | 5 | m3
Number of Shifts per day |  | 3 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | SBA Anion Regeneration |  |  | 501 | kg as 100% NaOH |  | Annualised Raw Water cost |  | 7430512.32 |  |  | Number of UF pressure vessels housings |  | 24 |  |  | Number of Skids (parallel operation) | 6 |  | Anion Resin Volume | 5 | m3
Duration of shift |  | 9 | hours |  | Total Number of Cation vessels |  |  | 3 |  |  | Total Number of Anion vessels |  |  | 3 |  |  | Total Number of MBIX vessels |  |  | 3 |  |  | SAC Cation Cost per Regeneration |  |  | 462 |  |  | Volume of effluent produced |  | 241746 | m3 per annum |  | Number of UF elements per housing |  | 4 |  |  | GTM Contactors per skid (series operation) | 4 |  | Resin Replacement Frequency | 2 | years
Average time spent per shift on demin plant |  | 5 | hours |  | Volume of cation resin per vessel |  |  | 14 | m3 |  | Volume of Anion resin per vessel |  |  | 11 | m3 |  | Volume of SAC Cation Resin per vessel |  |  | 14 | m3 |  | SBA Anion Cost per regeneration |  |  | 869.235 |  |  | Effluent solids loading per annum from Cations |  | 7289415 | equivalents |  | Total number of UF elements |  | 96 |  |  | Total number of contactors | 24 |  | Cation Resin Replacement Cost | 106300
Fraction of shift time spent on demin plant (average) |  | 55.56% |  |  | Total volume of cation resin |  |  | 42 | m3 |  | Total volume of Anion resin |  |  | 33 | m3 |  | Total volume of SAC Cation Resin |  |  | 42 | m3 |  | Annualised Acid Regenerant Cost for Cations |  |  | 303534 |  |  |  |  | 364.4708 | tonnes as CaCO3 |  | UF Element replacement Cost |  | 3326400 |  |  | Frequency of GTM replacement | 7 | years | Anion Resin Replacement Cost | 213300
Number of days per annum |  | 365 | days |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of SBA Anion Resin per vessel |  |  | 11 | m3 |  | Annualised Caustic Regenerant Cost for Anions |  |  | 571087.395 |  |  | Effluent solids loading p.a. from Anions |  | 3884184 | equivalents |  | UF element replacement frequency |  | 5 | years |  | Cost of GTM Replacement | 4419000
Plant availability |  | 90% |  |  | Total volume of inert resin |  |  | 3.3 | m3 |  | Total volume of inert resin |  |  | 3.3 | m3 |  | Total volume of SBA Anion Resin |  |  | 33 | m3 |  | Excess Acid per Cation Regeneration |  |  | 296.3 | kg as 100% H2SO4 |  |  |  | 194.2092 | tonnes as CaCO3 |  | UF system Recovery |  | 92.9 | % |  | Nitrogen sweep rate | 7.5 | Nm3/h
Number of operating days |  | 328.5 | days |  | Cation Resin Replacement Cost |  |  | 892920 |  |  | Anion Resin Replacement Cost |  |  | 977130 |  |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  |  |  |  | 6046.9388 | eq as SO42- |  | Effluent solids loading p.a. from MB Cations |  | 38270.25 | equivalents |  | UF System Backwash water |  | 18.1405 | m3/h |  | Nitrogen usage per annum | 59130 | Nm3
Number of manhours per annum on demin plant |  | 4380 | hours |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Total volume of Inert Resin |  |  | 3.3 | m3 |  | Excess Caustic per Anion Regeneration |  |  | 264.5 | kg as 100% NaOH |  |  |  | 1.9135 | tonnes as CaCO3 |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | Annualised usage @ 1.1455 kg/m3 @ NTP | 51619.3802 | kg
Annualised Labour Cost |  | 963600 |  |  | Total resin replacement cost |  |  | 947920 |  |  | Total resin replacement cost |  |  | 1032130 |  |  | Cation Resin Replacement Cost |  |  | 892920 | [5 empty] | 6612.5 | eq as Na+ |  | Effluent solids loading p.a. from MB Anions |  | 3668.25 | equivalents |  | UF Power Requirement |  | 0.2 | kWh/m3 |  | Annualised N2 costs | 412955.0415
[5 empty] | Frequency of resin replacement |  |  | 7 | years |  | Frequency of resin replacement |  |  | 5 | years |  | Anion Resin Replacement Cost |  |  | 1407780 |  |  | Additional Acid/Caustic for neutralisation per regeneration |  |  | 565.5612 | eq SO4 |  |  |  | 0.18341 | tonnes as CaCO3 |  | Annualised UF Power Usage |  | 402872.4 | kWh |  | Power requirement for GTM | 189 | kW
[5 empty] | Cation resin inlet flow per vessel |  |  | 170 | m3/h |  | Anion resin inlet flow per vessel |  |  | 170 | m3/h |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from Cation Regens |  | 3972838.7755 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 |  |  | Annualised GTM power usage | 1490076 | kWh
[5 empty] | Normal plant flow |  |  | 340 | m3/h |  | Normal plant flow |  |  | 340 | m3/h |  | Total resin replacement cost |  |  | 2355700 |  |  | MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  |  |  | 198.6419 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d |  | Annualised GTM power costs | 840402.864
[5 empty] | Maximum plant flow capability |  |  | 510 | m3/h |  | Maximum plant flow capability |  |  | 510 | m3/h |  | Frequency of resin replacement |  |  | 5 | years |  | MB Cation Cost Per Regeneration |  |  | 175.175 |  |  | Effluent solids loading p.a. from Anion Regens |  | 4344412.5 | equivalents |  |  |  | 1090.62 | L per annum
[5 empty] | Cation Bed Service run |  |  | 24 | hours |  | Anion Bed Service run |  |  | 24 | hours |  | Cation resin flow per vessel |  |  | 170 | m3/h |  | MB Anion Cost per Regeneration |  |  | 770.34 |  |  |  |  | 217.2206 | tonnes as CaCO3 |  | Annualised CEB NaOCl cost |  | 14897.8692
[5 empty] | Frequency of regeneration |  |  | 2 | per day |  | Frequency of regeneration |  |  | 2 | per day |  | Normal flow |  |  | 340 | m3/h |  | Annualised Acid Regenerant Cost for MB Cations |  |  | 9590.8312 |  |  | Effluent solids loading p.a. from MB Cation Regens |  | 355875 | equivalents |  | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[5 empty] | Ionic Load Removed per Service Run |  |  | 11095 | as eq |  | Ionic Load Removed per Service Run |  |  | 5912 | as eq |  | Maximum flow capability |  |  | 510 | m3/h |  | Annualised Caustic Regenerant Cost for MB Anions |  |  | 42176.115 |  |  |  |  | 17.7937 | tonnes as CaCO3 |  |  |  | 1304.145 | L per annum
[8 empty] | 554.75 | as kg CaCO3 |  |  |  |  | 295.6 | as kg CaCO3 |  | MBIX Service run |  |  | 288 | hours |  | Excess Acid per MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from MB Anion regens |  | 607725 | equivalents |  | Annualised CEB HCl cost |  | 930.2901
[5 empty] | Annual top-up Cation resin volume |  |  | 2.712 | m3 |  | Annual top-up Anion resin volume |  |  | 3.505 | m3 |  | Frequency of regeneration |  |  | 0.16667 | per day |  |  |  |  | 6500 | eq as SO42- |  |  |  | 30.3863 | tonnes as CaCO3
[5 empty] | Annual top-up resin cost |  |  | 57657.12 |  |  | Annual top-up resin cost |  |  | 103783.05 |  |  | Ionic Load Removed per Service Run - MB Cation |  |  | 699 | as eq |  | Excess Caustic per MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  | Effluent solids loading p.a. from Neutralisations |  | 371573.7245 | equivalents
[20 empty] | 34.95 | as kg CaCO3 |  |  |  |  | 11100 | eq as Na+ |  |  |  | 18.5787 | tonnes as CaCO3
[17 empty] | Ionic Load Removed per Service Run - MB Anion |  |  | 67 | as eq | [7 empty] | Total IX Effluent solids loading p.a. |  | 20867962.5 | equivalents
[20 empty] | 3.35 | as kg CaCO3 | [9 empty] | 1043.3981 | tonnes as CaCO3
[17 empty] | Annual top-up Cation resin volume |  |  | 2.712 | m3 | [7 empty] | IX Power Usage |  | 2828750 | kWh per annum
[17 empty] | Annual top-up resin cost |  |  | 57657.12 | [8 empty] | Annualised IX Power Costs |  | 1595415
[17 empty] | Annual top-up Anion resin volume |  |  | 3.505 | m3
[17 empty] | Annual top-up resin cost |  |  | 103783.05
Events/Activities |  |  | Year
Number | Description |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital Cost UF System |  | 30000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; Cat-Deg-An |  | 30000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; Polishing MB |  | 5000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  | 2187500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Capital cost; Bulk chemical off-loading bay |  | 8750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Annualised Labour Cost |  | 481800 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600
9 | SAC Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 947920 | 0 | 0 | 0 | 0 | 0 | 0 | 947920 | 0 | 0 | 0 | 0 | 0 | 0 | 947920 | 0 | 0 | 0 | 0 | 0 | 0 | 947920 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | SBA Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 1032130 | 0 | 0 | 0 | 0 | 0
11 | SAC MB Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 892920 | 0 | 0 | 0 | 0 | 0
12 | SBA MB Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 1407780 | 0 | 0 | 0 | 0 | 0
13 | SBA MB Inert Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 0
14 | NR-MBIX Cation Resin Replacement |  | 0 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0
15 | NR-MBIX Anion Resin Replacement |  | 0 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0
16 | UF Element Replacement |  | 0 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 3326400 | 0 | 0 | 0 | 0 | 0
17 | GTM Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Annualised IX Power Costs |  | 797707.5 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415 | 1595415
19 | Annualised UF Power Costs |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
20 | Annualised GTM Power Costs |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
21 | Annualised SAC Cation Regen Acid Costs |  | 151767 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534 | 303534
22 | Annualised SBA Anion Regen Caustic Costs |  | 285543.6975 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395 | 571087.395
23 | Annualised SAC MB Cation Regen Acid Costs |  | 4795.4156 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312
24 | Annualised SBA MB Anion Regen Caustic Costs |  | 21088.0575 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115
25 | Annualised SAC Cation Resin Top-up Cost |  | 28828.56 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12
26 | Annualised SBA Anion Resin Top-up Cost |  | 51891.525 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05
27 | Annualised SAC MB Cation Resin Top-up Cost |  | 28828.56 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12 | 57657.12
28 | Annualised SBA MB Anion Resin Top-up Cost |  | 51891.525 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05 | 103783.05
29 | Annualised UF Backwash water costs |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
30 | Annualised UF CEB NaOCl costs |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
31 | Annualised UF CEB HCl costs |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
32 | Annualised GTM N2 Costs |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
33 | Raw Water |  | 3715256.16 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32
| Total |  | 93303326.3568 | 13131652.7136 | 13451252.7136 | 13131652.7136 | 13451252.7136 | 19845882.7136 | 13451252.7136 | 18498572.7136 | 13451252.7136 | 13131652.7136 | 20165482.7136 | 13131652.7136 | 13451252.7136 | 13131652.7136 | 18818172.7136 | 19845882.7136 | 13451252.7136 | 13131652.7136 | 13451252.7136 | 13131652.7136 | 20165482.7136 | 18498572.7136 | 13451252.7136 | 13131652.7136 | 13451252.7136 | 19845882.7136 | 13451252.7136 | 13131652.7136 | 18818172.7136 | 13131652.7136 | 20165482.7136 | 13131652.7136 | 13451252.7136 | 13131652.7136 | 13451252.7136 | 13131652.7136
| Index |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  | 108124769.681 | 16381795.1583 | 18064205.6444 | 18984080.1782 | 20933745.3555 | 33248239.9013 | 24259117.9061 | 35914062.0332 | 28112733.3685 | 29544304.0675 | 48840154.8646 | 34237483.2433 | 37753673.0303 | 39676184.4909 | 61207127.2948 | 69487870.2544 | 50700862.4381 | 53282677.167 | 58754808.5134 | 61746750.321 | 102074526.4865 | 100800110.1508 | 78904096.606 | 82922090.561 | 91438189.8861 | 145227660.9777 | 105963352.0855 | 111359271.0103 | 171790235.4687 | 129048941.7687 | 213332840.2895 | 149548656.5287 | 164907304.6806 | 173304797.1028 | 191103201.0705 | 200834654.0584
| Discount |  | 92699562.4837 | 13004397.1624 | 13277730.4157 | 12920245.9804 | 13191810.4999 | 19400028.6418 | 13106446.5701 | 17965972.4376 | 13021635.0286 | 12671045.6056 | 19395097.4711 | 12589051.5346 | 12853654.8352 | 12507588.0454 | 17865777.0041 | 18780413.8318 | 12687841.6005 | 12346239.1016 | 12605738.8429 | 12266346.8467 | 18775640.1572 | 17167799.4168 | 12443123.7455 | 12108109.9347 | 12362604.552 | 18180588.8129 | 12282606.3966 | 11951914.2923 | 17072055.359 | 11874573.7049 | 18175967.6039 | 11797733.5869 | 12045704.5511 | 11721390.6997 | 11967757.0489 | 11645541.8256
| Actual Net Present Value |  | 92699562.4837 | 105703959.6462 | 118981690.0619 | 131901936.0423 | 145093746.5422 | 164493775.184 | 177600221.7542 | 195566194.1918 | 208587829.2204 | 221258874.826 | 240653972.2971 | 253243023.8317 | 266096678.6669 | 278604266.7123 | 296470043.7165 | 315250457.5483 | 327938299.1488 | 340284538.2504 | 352890277.0933 | 365156623.94 | 383932264.0971 | 401100063.514 | 413543187.2595 | 425651297.1942 | 438013901.7462 | 456194490.5591 | 468477096.9557 | 480429011.248 | 497501066.607 | 509375640.312 | 527551607.9159 | 539349341.5028 | 551395046.0539 | 563116436.7535 | 575084193.8024 | 586729735.6281
| Actual Net Present Value ( x R 1000) |  | 92699.5625 | 105703.9596 | 118981.6901 | 131901.936 | 145093.7465 | 164493.7752 | 177600.2218 | 195566.1942 | 208587.8292 | 221258.8748 | 240653.9723 | 253243.0238 | 266096.6787 | 278604.2667 | 296470.0437 | 315250.4575 | 327938.2991 | 340284.5383 | 352890.2771 | 365156.6239 | 383932.2641 | 401100.0635 | 413543.1873 | 425651.2972 | 438013.9017 | 456194.4906 | 468477.097 | 480429.0112 | 497501.0666 | 509375.6403 | 527551.6079 | 539349.3415 | 551395.0461 | 563116.4368 | 575084.1938 | 586729.7356

## IX-Mix
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 2:
Ion Exchange-Based System: Conventional Primary Exchangers and Polishing Mixed Beds Configuration : Raw → UF → Cation (SAC) → Vacuum Degasser → Anion (SBA) → MBIX → GTM → NRMB?
Results
Net Present Value this Scenario |  |  | 1198383289.5154
Manpower: |  |  |  |  | IX Cation Data : SAC - Amberjet 1500 H | [5 empty] | IX Anion Data : SBA - Amberjet 4200 Cl | [5 empty] | Mixed Bed (regenerable) Data : SAC/SBA - Amberjet 1500 H/ Ambersep 900 OH | [5 empty] | Chemical usage : | [5 empty] | IX Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data : |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
Number of Chemist/Operators for WTP per shift |  | 1 |  |  | Number of Trains |  |  | 15 |  |  | Number of Trains |  |  | 15 |  |  | Number of Trains |  |  | 3 |  |  | SAC Cation Regeneration |  |  | 840 | kg as 100% H2SO4 |  | Raw Water Usage for demin production |  | 2680560 | m3 per annum |  | Flow to UF plant |  | 255.5 | m3/h |  | Flow through GTM | 320 | m3/h | Cation Resin Volume | 5 | m3
Number of Shifts per day |  | 3 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | SBA Anion Regeneration |  |  | 501 | kg as 100% NaOH |  | Annualised Raw Water cost |  | 7430512.32 |  |  | Number of UF pressure vessels housings |  | 36 |  |  | Number of Skids (parallel operation) | 6 |  | Anion Resin Volume | 5 | m3
Duration of shift |  | 9 | hours |  | Total Number of Cation vessels |  |  | 15 |  |  | Total Number of Anion vessels |  |  | 15 |  |  | Total Number of MBIX vessels |  |  | 3 |  |  | SAC Cation Cost per Regeneration |  |  | 462 |  |  | Volume of effluent produced |  | 241746 | m3 per annum |  | Number of UF elements per housing |  | 4 |  |  | GTM Contactors per skid (series operation) | 4 |  | Resin Replacement Frequency | 2 | years
Average time spent per shift on demin plant |  | 5 | hours |  | Volume of cation resin per vessel |  |  | 14 | m3 |  | Volume of Anion resin per vessel |  |  | 11 | m3 |  | Volume of SAC Cation Resin per vessel |  |  | 14 | m3 |  | SBA Anion Cost per regeneration |  |  | 869.235 |  |  | Effluent solids loading per annum from Cations |  | 36447075 | equivalents |  | Total number of UF elements |  | 144 |  |  | Total number of contactors | 24 |  | Cation Resin Replacement Cost | 106300
Fraction of shift time spent on demin plant (average) |  | 55.56% |  |  | Total volume of cation resin |  |  | 210 | m3 |  | Total volume of Anion resin |  |  | 165 | m3 |  | Total volume of SAC Cation Resin |  |  | 42 | m3 |  | Annualised Acid Regenerant Cost for Cations |  |  | 1517670 |  |  |  |  | 1822.3537 | tonnes as CaCO3 |  | UF Element replacement Cost |  | 4989600 |  |  | Frequency of GTM replacement | 7 | years | Anion Resin Replacement Cost | 213300
Number of days per annum |  | 365 | days |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of SBA Anion Resin per vessel |  |  | 11 | m3 |  | Annualised Caustic Regenerant Cost for Anions |  |  | 2855436.975 |  |  | Effluent solids loading p.a. from Anions |  | 19420920 | equivalents |  | UF element replacement frequency |  | 5 | years |  | Cost of GTM Replacement | 4419000
Plant availability |  | 90% |  |  | Total volume of inert resin |  |  | 16.5 | m3 |  | Total volume of inert resin |  |  | 16.5 | m3 |  | Total volume of SBA Anion Resin |  |  | 33 | m3 |  | Excess Acid per Cation Regeneration |  |  | 296.3 | kg as 100% H2SO4 |  |  |  | 971.046 | tonnes as CaCO3 |  | UF system Recovery |  | 92.9 | % |  | Nitrogen sweep rate | 7.5 | Nm3/h
Number of operating days |  | 328.5 | days |  | Cation Resin Replacement Cost |  |  | 4464600 |  |  | Anion Resin Replacement Cost |  |  | 4885650 |  |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  |  |  |  | 6046.9388 | eq as SO42- |  | Effluent solids loading p.a. from MB Cations |  | 38270.25 | equivalents |  | UF System Backwash water |  | 18.1405 | m3/h |  | Nitrogen usage per annum | 59130 | Nm3
Number of manhours per annum on demin plant |  | 4380 | hours |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Total volume of Inert Resin |  |  | 3.3 | m3 |  | Excess Caustic per Anion Regeneration |  |  | 264.5 | kg as 100% NaOH |  |  |  | 1.9135 | tonnes as CaCO3 |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | Annualised usage @ 1.1455 kg/m3 @ NTP | 51619.3802 | kg
Annualised Labour Cost |  | 963600 |  |  | Total resin replacement cost |  |  | 4519600 |  |  | Total resin replacement cost |  |  | 4940650 |  |  | Cation Resin Replacement Cost |  |  | 4464600 | [5 empty] | 6612.5 | eq as Na+ |  | Effluent solids loading p.a. from MB Anions |  | 3668.25 | equivalents |  | UF Power Requirement |  | 0.2 | kWh/m3 |  | Annualised N2 costs | 412955.0415
[5 empty] | Frequency of resin replacement |  |  | 7 | years |  | Frequency of resin replacement |  |  | 5 | years |  | Anion Resin Replacement Cost |  |  | 7038900 |  |  | Additional Acid/Caustic for neutralisation per regeneration |  |  | 565.5612 | eq SO4 |  |  |  | 0.18341 | tonnes as CaCO3 |  | Annualised UF Power Usage |  | 402872.4 | kWh |  | Power requirement for GTM | 189 | kW
[5 empty] | Cation resin inlet flow per vessel |  |  | 170 | m3/h |  | Anion resin inlet flow per vessel |  |  | 170 | m3/h |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from Cation Regens |  | 19864193.8776 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 |  |  | Annualised GTM power usage | 1490076 | kWh
[5 empty] | Normal plant flow |  |  | 340 | m3/h |  | Normal plant flow |  |  | 340 | m3/h |  | Total resin replacement cost |  |  | 11558500 |  |  | MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  |  |  | 993.2097 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d |  | Annualised GTM power costs | 840402.864
[5 empty] | Maximum plant flow capability |  |  | 510 | m3/h |  | Maximum plant flow capability |  |  | 510 | m3/h |  | Frequency of resin replacement |  |  | 5 | years |  | MB Cation Cost Per Regeneration |  |  | 175.175 |  |  | Effluent solids loading p.a. from Anion Regens |  | 21722062.5 | equivalents |  |  |  | 1090.62 | L per annum
[5 empty] | Cation Bed Service run |  |  | 24 | hours |  | Anion Bed Service run |  |  | 24 | hours |  | Cation resin flow per vessel |  |  | 170 | m3/h |  | MB Anion Cost per Regeneration |  |  | 770.34 |  |  |  |  | 1086.1031 | tonnes as CaCO3 |  | Annualised CEB NaOCl cost |  | 14897.8692
[5 empty] | Frequency of regeneration |  |  | 10 | per day |  | Frequency of regeneration |  |  | 10 | per day |  | Normal flow |  |  | 340 | m3/h |  | Annualised Acid Regenerant Cost for MB Cations |  |  | 9590.8312 |  |  | Effluent solids loading p.a. from MB Cation Regens |  | 355875 | equivalents |  | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[5 empty] | Ionic Load Removed per Service Run |  |  | 11095 | as eq |  | Ionic Load Removed per Service Run |  |  | 5912 | as eq |  | Maximum flow capability |  |  | 510 | m3/h |  | Annualised Caustic Regenerant Cost for MB Anions |  |  | 42176.115 |  |  |  |  | 17.7937 | tonnes as CaCO3 |  |  |  | 1304.145 | L per annum
[8 empty] | 554.75 | as kg CaCO3 |  |  |  |  | 295.6 | as kg CaCO3 |  | MBIX Service run |  |  | 288 | hours |  | Excess Acid per MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from MB Anion regens |  | 607725 | equivalents |  | Annualised CEB HCl cost |  | 930.2901
[5 empty] | Annual top-up Cation resin volume |  |  | 13.56 | m3 |  | Annual top-up Anion resin volume |  |  | 17.525 | m3 |  | Frequency of regeneration |  |  | 0.16667 | per day |  |  |  |  | 6500 | eq as SO42- |  |  |  | 30.3863 | tonnes as CaCO3
[5 empty] | Annual top-up resin cost |  |  | 288285.6 |  |  | Annual top-up resin cost |  |  | 518915.25 |  |  | Ionic Load Removed per Service Run - MB Cation |  |  | 699 | as eq |  | Excess Caustic per MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  | Effluent solids loading p.a. from Neutralisations |  | 1857868.6224 | equivalents
[20 empty] | 34.95 | as kg CaCO3 |  |  |  |  | 11100 | eq as Na+ |  |  |  | 92.8934 | tonnes as CaCO3
[17 empty] | Ionic Load Removed per Service Run - MB Anion |  |  | 67 | as eq | [7 empty] | Total IX Effluent solids loading p.a. |  | 100317658.5 | equivalents
[20 empty] | 3.35 | as kg CaCO3 | [9 empty] | 5015.8829 | tonnes as CaCO3
[17 empty] | Annual top-up Cation resin volume |  |  | 2.712 | m3 | [7 empty] | IX Power Usage |  | 14143750 | kWh per annum
[17 empty] | Annual top-up resin cost |  |  | 288285.6 | [8 empty] | Annualised IX Power Costs |  | 7977075
[17 empty] | Annual top-up Anion resin volume |  |  | 3.505 | m3
[17 empty] | Annual top-up resin cost |  |  | 518915.25
Events/Activities |  |  | Year
Number | Description |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital Cost UF System |  | 45000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; Cat-Deg-An |  | 150000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; Polishing MB |  | 5000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  | 10937500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Capital cost; Bulk chemical off-loading bay |  | 8750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Annualised Labour Cost |  | 481800 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600 | 963600
9 | SAC Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4519600 | 0 | 0 | 0 | 0 | 0 | 0 | 4519600 | 0 | 0 | 0 | 0 | 0 | 0 | 4519600 | 0 | 0 | 0 | 0 | 0 | 0 | 4519600 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | SBA Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 4940650 | 0 | 0 | 0 | 0 | 0
11 | SAC MB Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 4464600 | 0 | 0 | 0 | 0 | 0
12 | SBA MB Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 7038900 | 0 | 0 | 0 | 0 | 0
13 | SBA MB Inert Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 0
14 | NR-MBIX Cation Resin Replacement |  | 0 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0
15 | NR-MBIX Anion Resin Replacement |  | 0 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0
16 | UF Element Replacement |  | 0 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 4989600 | 0 | 0 | 0 | 0 | 0
17 | GTM Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Annualised IX Power Costs |  | 3988537.5 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075 | 7977075
19 | Annualised UF Power Costs |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
20 | Annualised GTM Power Costs |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
21 | Annualised SAC Cation Regen Acid Costs |  | 758835 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670 | 1517670
22 | Annualised SBA Anion Regen Caustic Costs |  | 1427718.4875 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975 | 2855436.975
23 | Annualised SAC MB Cation Regen Acid Costs |  | 4795.4156 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312
24 | Annualised SBA MB Anion Regen Caustic Costs |  | 21088.0575 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115
25 | Annualised SAC Cation Resin Top-up Cost |  | 144142.8 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6
26 | Annualised SBA Anion Resin Top-up Cost |  | 259457.625 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25
27 | Annualised SAC MB Cation Resin Top-up Cost |  | 144142.8 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6 | 288285.6
28 | Annualised SBA MB Anion Resin Top-up Cost |  | 259457.625 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25 | 518915.25
29 | Annualised UF Backwash water costs |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
30 | Annualised UF CEB NaOCl costs |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
31 | Annualised UF CEB HCl costs |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
32 | Annualised GTM N2 Costs |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
33 | Raw Water |  | 3715256.16 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32
| Total |  | 242639159.8268 | 24303319.6536 | 24622919.6536 | 24303319.6536 | 24622919.6536 | 45792069.6536 | 24622919.6536 | 33241919.6536 | 24622919.6536 | 24303319.6536 | 46111669.6536 | 24303319.6536 | 24622919.6536 | 24303319.6536 | 33561519.6536 | 45792069.6536 | 24622919.6536 | 24303319.6536 | 24622919.6536 | 24303319.6536 | 46111669.6536 | 33241919.6536 | 24622919.6536 | 24303319.6536 | 24622919.6536 | 45792069.6536 | 24622919.6536 | 24303319.6536 | 33561519.6536 | 24303319.6536 | 46111669.6536 | 24303319.6536 | 24622919.6536 | 24303319.6536 | 24622919.6536 | 24303319.6536
| Index |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  | 281182936.3034 | 30318499.3477 | 33067067.7043 | 35134661.1857 | 38319845.8101 | 76716452.4448 | 44407039.5367 | 64537539.3566 | 51461197.6829 | 54678925.9019 | 111680990.6778 | 63364796.3091 | 69109225.5455 | 73430436.7735 | 109160662.7758 | 160335190.9661 | 92809442.2701 | 98612563.3562 | 107552430.996 | 114277390.9236 | 233410075.6351 | 181137713.411 | 144436304.3681 | 153467512.2168 | 167380336.2986 | 335095962.3766 | 193969079.3254 | 206097436.3841 | 306381573.3723 | 238836477.8729 | 487820380.8664 | 276776189.7651 | 301867744.2096 | 320742710.2557 | 349820114.5797 | 371693411.451
| Discount |  | 241069046.8993 | 24067802.2816 | 24305281.9071 | 23912060.0365 | 24148002.9364 | 44763313.1601 | 23991741.7145 | 32284837.4043 | 23836491.6558 | 23450854.0863 | 44350057.9774 | 23299104.1001 | 23528998.897 | 23148336.0849 | 31862956.8969 | 43333623.9422 | 23225472.8209 | 22849720.5912 | 23075181.2721 | 22701860.5273 | 42933567.6591 | 30850521.1553 | 22777509.4818 | 22409004.6061 | 22630116.6944 | 41949597.3688 | 22483677.6827 | 22119926.5511 | 30447383.5041 | 21976788.9691 | 41562318.4276 | 21834577.6274 | 22050021.7821 | 21693286.5323 | 21907336.5525 | 21552909.729
| Actual Net Present Value |  | 241069046.8993 | 265136849.1809 | 289442131.088 | 313354191.1245 | 337502194.0609 | 382265507.221 | 406257248.9355 | 438542086.3399 | 462378577.9956 | 485829432.082 | 530179490.0594 | 553478594.1595 | 577007593.0565 | 600155929.1414 | 632018886.0383 | 675352509.9805 | 698577982.8014 | 721427703.3926 | 744502884.6648 | 767204745.1921 | 810138312.8511 | 840988834.0065 | 863766343.4882 | 886175348.0943 | 908805464.7887 | 950755062.1575 | 973238739.8402 | 995358666.3913 | 1025806049.8954 | 1047782838.8645 | 1089345157.2921 | 1111179734.9195 | 1133229756.7016 | 1154923043.2339 | 1176830379.7864 | 1198383289.5154
| Actual Net Present Value ( x R 1000) |  | 241069.0469 | 265136.8492 | 289442.1311 | 313354.1911 | 337502.1941 | 382265.5072 | 406257.2489 | 438542.0863 | 462378.578 | 485829.4321 | 530179.4901 | 553478.5942 | 577007.5931 | 600155.9291 | 632018.886 | 675352.51 | 698577.9828 | 721427.7034 | 744502.8847 | 767204.7452 | 810138.3129 | 840988.834 | 863766.3435 | 886175.3481 | 908805.4648 | 950755.0622 | 973238.7398 | 995358.6664 | 1025806.0499 | 1047782.8389 | 1089345.1573 | 1111179.7349 | 1133229.7567 | 1154923.0432 | 1176830.3798 | 1198383.2895

## IX-Croc
Medupi PS : WTP Life Cycle Cost Analysis
Scenario 2:
Ion Exchange-Based System: Conventional Primary Exchangers and Polishing Mixed Beds Configuration : Raw → UF → Cation (SAC) → Vacuum Degasser → Anion (SBA) → MBIX → GTM → NRMB?
Results
NPV this Scenario |  |  | 2175690645.1646
Manpower: |  |  |  |  | IX Cation Data : SAC - Amberjet 1500 H | [5 empty] | IX Anion Data : SBA - Amberjet 4200 Cl | [5 empty] | Mixed Bed (regenerable) Data : SAC/SBA - Amberjet 1500 H/ Ambersep 900 OH | [5 empty] | Chemical usage : | [5 empty] | IX Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data : |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
Number of Chemist/Operators for WTP per shift |  | 2 |  |  | Number of Trains |  |  | 31 |  |  | Number of Trains |  |  | 31 |  |  | Number of Trains |  |  | 3 |  |  | SAC Cation Regeneration |  |  | 840 | kg as 100% H2SO4 |  | Raw Water Usage for demin production |  | 2680560 | m3 per annum |  | Flow to UF plant |  | 255.5 | m3/h |  | Flow through GTM | 320 | m3/h | Cation Resin Volume | 5 | m3
Number of Shifts per day |  | 3 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | SBA Anion Regeneration |  |  | 501 | kg as 100% NaOH |  | Annualised Raw Water cost |  | 7430512.32 |  |  | Number of UF pressure vessels housings |  | 48 |  |  | Number of Skids (parallel operation) | 6 |  | Anion Resin Volume | 5 | m3
Duration of shift |  | 9 | hours |  | Total Number of Cation vessels |  |  | 31 |  |  | Total Number of Anion vessels |  |  | 31 |  |  | Total Number of MBIX vessels |  |  | 3 |  |  | SAC Cation Cost per Regeneration |  |  | 462 |  |  | Volume of effluent produced |  | 241746 | m3 per annum |  | Number of UF elements per housing |  | 4 |  |  | GTM Contactors per skid (series operation) | 4 |  | Resin Replacement Frequency | 2 | years
Average time spent per shift on demin plant |  | 5 | hours |  | Volume of cation resin per vessel |  |  | 14 | m3 |  | Volume of Anion resin per vessel |  |  | 11 | m3 |  | Volume of SAC Cation Resin per vessel |  |  | 14 | m3 |  | SBA Anion Cost per regeneration |  |  | 869.235 |  |  | Effluent solids loading per annum from Cations |  | 112985932.5 | equivalents |  | Total number of UF elements |  | 192 |  |  | Total number of contactors | 24 |  | Cation Resin Replacement Cost | 106300
Fraction of shift time spent on demin plant (average) |  | 55.56% |  |  | Total volume of cation resin |  |  | 434 | m3 |  | Total volume of Anion resin |  |  | 341 | m3 |  | Total volume of SAC Cation Resin |  |  | 42 | m3 |  | Annualised Acid Regenerant Cost for Cations |  |  | 4704777 |  |  |  |  | 5649.2966 | tonnes as CaCO3 |  | UF Element replacement Cost |  | 6652800 |  |  | Frequency of GTM replacement | 7 | years | Anion Resin Replacement Cost | 213300
Number of days per annum |  | 365 | days |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of SBA Anion Resin per vessel |  |  | 11 | m3 |  | Annualised Caustic Regenerant Cost for Anions |  |  | 8851854.6225 |  |  | Effluent solids loading p.a. from Anions |  | 60204852 | equivalents |  | UF element replacement frequency |  | 5 | years |  | Cost of GTM Replacement | 4419000
Plant availability |  | 90% |  |  | Total volume of inert resin |  |  | 34.1 | m3 |  | Total volume of inert resin |  |  | 34.1 | m3 |  | Total volume of SBA Anion Resin |  |  | 33 | m3 |  | Excess Acid per Cation Regeneration |  |  | 296.3 | kg as 100% H2SO4 |  |  |  | 3010.2426 | tonnes as CaCO3 |  | UF system Recovery |  | 92.9 | % |  | Nitrogen sweep rate | 7.5 | Nm3/h
Number of operating days |  | 328.5 | days |  | Cation Resin Replacement Cost |  |  | 9226840 |  |  | Anion Resin Replacement Cost |  |  | 10097010 |  |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  |  |  |  | 6046.9388 | eq as SO42- |  | Effluent solids loading p.a. from MB Cations |  | 38270.25 | equivalents |  | UF System Backwash water |  | 18.1405 | m3/h |  | Nitrogen usage per annum | 59130 | Nm3
Number of manhours per annum on demin plant |  | 8760 | hours |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Total volume of Inert Resin |  |  | 3.3 | m3 |  | Excess Caustic per Anion Regeneration |  |  | 264.5 | kg as 100% NaOH |  |  |  | 1.9135 | tonnes as CaCO3 |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | Annualised usage @ 1.1455 kg/m3 @ NTP | 51619.3802 | kg
Annualised Labour Cost |  | 1927200 |  |  | Total resin replacement cost |  |  | 9281840 |  |  | Total resin replacement cost |  |  | 10152010 |  |  | Cation Resin Replacement Cost |  |  | 9226840 | [5 empty] | 6612.5 | eq as Na+ |  | Effluent solids loading p.a. from MB Anions |  | 3668.25 | equivalents |  | UF Power Requirement |  | 0.2 | kWh/m3 |  | Annualised N2 costs | 412955.0415
[5 empty] | Frequency of resin replacement |  |  | 7 | years |  | Frequency of resin replacement |  |  | 5 | years |  | Anion Resin Replacement Cost |  |  | 14547060 |  |  | Additional Acid/Caustic for neutralisation per regeneration |  |  | 565.5612 | eq SO4 |  |  |  | 0.18341 | tonnes as CaCO3 |  | Annualised UF Power Usage |  | 402872.4 | kWh |  | Power requirement for GTM | 189 | kW
[5 empty] | Cation resin inlet flow per vessel |  |  | 170 | m3/h |  | Anion resin inlet flow per vessel |  |  | 170 | m3/h |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from Cation Regens |  | 61579001.0204 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 |  |  | Annualised GTM power usage | 1490076 | kWh
[5 empty] | Normal plant flow |  |  | 340 | m3/h |  | Normal plant flow |  |  | 340 | m3/h |  | Total resin replacement cost |  |  | 23828900 |  |  | MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  |  |  | 3078.9501 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d |  | Annualised GTM power costs | 840402.864
[5 empty] | Maximum plant flow capability |  |  | 510 | m3/h |  | Maximum plant flow capability |  |  | 510 | m3/h |  | Frequency of resin replacement |  |  | 5 | years |  | MB Cation Cost Per Regeneration |  |  | 175.175 |  |  | Effluent solids loading p.a. from Anion Regens |  | 67338393.75 | equivalents |  |  |  | 1090.62 | L per annum
[5 empty] | Cation Bed Service run |  |  | 24 | hours |  | Anion Bed Service run |  |  | 24 | hours |  | Cation resin flow per vessel |  |  | 170 | m3/h |  | MB Anion Cost per Regeneration |  |  | 770.34 |  |  |  |  | 3366.9197 | tonnes as CaCO3 |  | Annualised CEB NaOCl cost |  | 14897.8692
[5 empty] | Frequency of regeneration |  |  | 31 | per day |  | Frequency of regeneration |  |  | 31 | per day |  | Normal flow |  |  | 340 | m3/h |  | Annualised Acid Regenerant Cost for MB Cations |  |  | 9590.8312 |  |  | Effluent solids loading p.a. from MB Cation Regens |  | 355875 | equivalents |  | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[5 empty] | Ionic Load Removed per Service Run |  |  | 11095 | as eq |  | Ionic Load Removed per Service Run |  |  | 5912 | as eq |  | Maximum flow capability |  |  | 510 | m3/h |  | Annualised Caustic Regenerant Cost for MB Anions |  |  | 42176.115 |  |  |  |  | 17.7937 | tonnes as CaCO3 |  |  |  | 1304.145 | L per annum
[8 empty] | 554.75 | as kg CaCO3 |  |  |  |  | 295.6 | as kg CaCO3 |  | MBIX Service run |  |  | 288 | hours |  | Excess Acid per MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from MB Anion regens |  | 607725 | equivalents |  | Annualised CEB HCl cost |  | 930.2901
[5 empty] | Annual top-up Cation resin volume |  |  | 27.6624 | m3 |  | Annual top-up Anion resin volume |  |  | 35.751 | m3 |  | Frequency of regeneration |  |  | 0.16667 | per day |  |  |  |  | 6500 | eq as SO42- |  |  |  | 30.3863 | tonnes as CaCO3
[5 empty] | Annual top-up resin cost |  |  | 588102.624 |  |  | Annual top-up resin cost |  |  | 1058587.11 |  |  | Ionic Load Removed per Service Run - MB Cation |  |  | 699 | as eq |  | Excess Caustic per MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  | Effluent solids loading p.a. from Neutralisations |  | 5759392.7296 | equivalents
[20 empty] | 34.95 | as kg CaCO3 |  |  |  |  | 11100 | eq as Na+ |  |  |  | 287.9696 | tonnes as CaCO3
[17 empty] | Ionic Load Removed per Service Run - MB Anion |  |  | 67 | as eq | [7 empty] | Total IX Effluent solids loading p.a. |  | 308873110.5 | equivalents
[20 empty] | 3.35 | as kg CaCO3 | [9 empty] | 15443.6555 | tonnes as CaCO3
[17 empty] | Annual top-up Cation resin volume |  |  | 2.712 | m3 | [7 empty] | IX Power Usage |  | 28853250 | kWh per annum
[17 empty] | Annual top-up resin cost |  |  | 588102.624 | [8 empty] | Annualised IX Power Costs |  | 16273233
[17 empty] | Annual top-up Anion resin volume |  |  | 3.505 | m3
[17 empty] | Annual top-up resin cost |  |  | 1058587.11
Events/Activities |  |  | Year
Number | Description |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital Cost UF System |  | 60000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital cost; Cat-Deg-An |  | 306000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Capital Cost; Polishing MB |  | 5000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Capital cost; GTM system |  | 9000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Capital cost; NR-MBIX |  | 1800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Capital cost; Bulk chemical storage & dilution |  | 22312500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Capital cost; Bulk chemical off-loading bay |  | 8750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Annualised Labour Cost |  | 963600 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200 | 1927200
9 | SAC Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9281840 | 0 | 0 | 0 | 0 | 0 | 0 | 9281840 | 0 | 0 | 0 | 0 | 0 | 0 | 9281840 | 0 | 0 | 0 | 0 | 0 | 0 | 9281840 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | SBA Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 10152010 | 0 | 0 | 0 | 0 | 0
11 | SAC MB Cation Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 9226840 | 0 | 0 | 0 | 0 | 0
12 | SBA MB Anion Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 14547060 | 0 | 0 | 0 | 0 | 0
13 | SBA MB Inert Resin Replacement |  | 0 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 55000 | 0 | 0 | 0 | 0 | 0
14 | NR-MBIX Cation Resin Replacement |  | 0 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0 | 106300 | 0
15 | NR-MBIX Anion Resin Replacement |  | 0 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0 | 213300 | 0
16 | UF Element Replacement |  | 0 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 6652800 | 0 | 0 | 0 | 0 | 0
17 | GTM Replacement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 4419000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Annualised IX Power Costs |  | 8136616.5 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233 | 16273233
19 | Annualised UF Power Costs |  | 113610.0168 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336 | 227220.0336
20 | Annualised GTM Power Costs |  | 420201.432 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864 | 840402.864
21 | Annualised SAC Cation Regen Acid Costs |  | 2352388.5 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777 | 4704777
22 | Annualised SBA Anion Regen Caustic Costs |  | 4425927.3113 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225 | 8851854.6225
23 | Annualised SAC MB Cation Regen Acid Costs |  | 4795.4156 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312 | 9590.8312
24 | Annualised SBA MB Anion Regen Caustic Costs |  | 21088.0575 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115 | 42176.115
25 | Annualised SAC Cation Resin Top-up Cost |  | 294051.312 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624
26 | Annualised SBA Anion Resin Top-up Cost |  | 529293.555 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11
27 | Annualised SAC MB Cation Resin Top-up Cost |  | 294051.312 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624 | 588102.624
28 | Annualised SBA MB Anion Resin Top-up Cost |  | 529293.555 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11 | 1058587.11
29 | Annualised UF Backwash water costs |  | 198225.307 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139 | 396450.6139
30 | Annualised UF CEB NaOCl costs |  | 7448.9346 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692 | 14897.8692
31 | Annualised UF CEB HCl costs |  | 465.1451 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901 | 930.2901
32 | Annualised GTM N2 Costs |  | 206477.5207 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415 | 412955.0415
33 | Raw Water |  | 3715256.16 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32 | 7430512.32
| Total |  | 435075290.0345 | 44425580.0691 | 44745180.0691 | 44425580.0691 | 44745180.0691 | 85059290.0691 | 44745180.0691 | 58126420.0691 | 44745180.0691 | 44425580.0691 | 85378890.0691 | 44425580.0691 | 44745180.0691 | 44425580.0691 | 58446020.0691 | 85059290.0691 | 44745180.0691 | 44425580.0691 | 44745180.0691 | 44425580.0691 | 85378890.0691 | 58126420.0691 | 44745180.0691 | 44425580.0691 | 44745180.0691 | 85059290.0691 | 44745180.0691 | 44425580.0691 | 58446020.0691 | 44425580.0691 | 85378890.0691 | 44425580.0691 | 44745180.0691 | 44425580.0691 | 44745180.0691 | 44425580.0691
| Index |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  | 504187978.7759 | 55421108.7023 | 60090026.6745 | 64224876.5171 | 69635462.6143 | 142501682.7355 | 80697212.5304 | 112849563.5018 | 93516146.3096 | 99951078.0986 | 206784943.9746 | 115828531.7444 | 125586436.7417 | 134228154.6262 | 190098849.9093 | 297824440.3417 | 168654865.6664 | 180260161.6423 | 195446070.551 | 208894893.9045 | 432174617.3666 | 316735222.5686 | 262472060.1127 | 280533003.2758 | 304166337.4237 | 622444560.3879 | 352483844.4977 | 376738581.0921 | 533551036.1554 | 436584352.3603 | 903232586.9862 | 505936759.0476 | 548559097.0421 | 586305951.58 | 635698943.8653 | 679441971.1769
| Discount |  | 432259926.9341 | 43995062.9209 | 44167963.4611 | 43710371.7891 | 43882153.4935 | 83148363.1849 | 43598192.9962 | 56452877.583 | 43316070.0014 | 42867304.1688 | 82117146.3331 | 42589910.7403 | 42757289.0342 | 42314312.3188 | 55488042.1828 | 80492699.206 | 42205716.3887 | 41768454.1105 | 41932604.0809 | 41498171.3177 | 79494418.2455 | 53944849.4766 | 41391669.9411 | 40962841.3973 | 41123825.3108 | 77921854.1086 | 40857713.8975 | 40434417.2781 | 53022878.7523 | 40172767.0098 | 76955457.1045 | 39912809.8748 | 40069667.1658 | 39654534.9171 | 39810377.1878 | 39397931.2512
| Actual Net Present Value |  | 432259926.9341 | 476254989.855 | 520422953.3161 | 564133325.1052 | 608015478.5987 | 691163841.7836 | 734762034.7798 | 791214912.3628 | 834530982.3642 | 877398286.533 | 959515432.8661 | 1002105343.6064 | 1044862632.6406 | 1087176944.9594 | 1142664987.1422 | 1223157686.3482 | 1265363402.7369 | 1307131856.8473 | 1349064460.9282 | 1390562632.2459 | 1470057050.4914 | 1524001899.9679 | 1565393569.909 | 1606356411.3063 | 1647480236.6171 | 1725402090.7257 | 1766259804.6231 | 1806694221.9013 | 1859717100.6536 | 1899889867.6633 | 1976845324.7679 | 2016758134.6427 | 2056827801.8085 | 2096482336.7256 | 2136292713.9134 | 2175690645.1646
| Actual Net Present Value ( x R 1000) |  | 432259.9269 | 476254.9899 | 520422.9533 | 564133.3251 | 608015.4786 | 691163.8418 | 734762.0348 | 791214.9124 | 834530.9824 | 877398.2865 | 959515.4329 | 1002105.3436 | 1044862.6326 | 1087176.945 | 1142664.9871 | 1223157.6863 | 1265363.4027 | 1307131.8568 | 1349064.4609 | 1390562.6322 | 1470057.0505 | 1524001.9 | 1565393.5699 | 1606356.4113 | 1647480.2366 | 1725402.0907 | 1766259.8046 | 1806694.2219 | 1859717.1007 | 1899889.8677 | 1976845.3248 | 2016758.1346 | 2056827.8018 | 2096482.3367 | 2136292.7139 | 2175690.6452

## IX-Mo-dataSummary
Scenario 2:
Mokolo Water Supply Only: Ion Exchange-Based System - Conventional Primary Exchangers and Polishing Mixed Beds Configuration : Raw → UF → Cation (SAC) → Vacuum Degasser → Anion (SBA) → MBIX → GTM → NRMB
Results
Net Present Value this Scenario |  |  | 586729735.6281
Manpower:
Number of Chemist/Operators for WTP per shift |  | 1
Number of Shifts per day |  | 3
Duration of shift |  | 9 | hours
Average time spent per shift on demin plant |  | 5 | hours
Fraction of shift time spent on demin plant (average) |  | 55.56%
Number of days per annum |  | 365 | days
Plant availability |  | 90%
Number of operating days |  | 328.5 | days
Number of manhours per annum on demin plant |  | 4380 | hours
Annualised Labour Cost |  | 385440
UF Plant Data : |  |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
Flow to UF plant | 255.5 | m3/h |  | Cation Resin Volume | 5 | m3
Number of UF pressure vessels housings | 24 |  |  | Anion Resin Volume | 5 | m3
Number of UF elements per housing | 4 |  |  | Resin Replacement Frequency | 2 | years
Total number of UF elements | 96 |  |  | Cation Resin Replacement Cost | 106300
UF Element replacement Cost | 3326400 |  |  | Anion Resin Replacement Cost | 213300
UF element replacement frequency | 5 | years
UF system Recovery | 92.9 | %
UF System Backwash water | 18.1405 | m3/h
Annualised Backwash replacement water cost | 396450.6139
UF Power Requirement | 0.2 | kWh/m3
Annualised UF Power Usage | 402872.4 | kWh
Annualised UF Power Cost | 227220.0336
CEB Sodium hypochlorite usage | 3.32 | L/d
| 1090.62 | L per annum
Annualised CEB NaOCl cost | 14897.8692
CEB Hydrochloric Acid usage | 3.97 | L/d
| 1304.145 | L per annum
Annualised CEB HCl cost | 930.2901
IX Cation Data : SAC - Amberjet 1500 H |  |  |  | IX Anion Data : SBA - Amberjet 4200 Cl
Number of Trains |  | 3 |  | Number of Trains |  | 3
Number of Vessels per train |  | 1 |  | Number of Vessels per train |  | 1
Total Number of Cation vessels |  | 3 |  | Total Number of Anion vessels |  | 3
Volume of cation resin per vessel |  | 14 | m3 | Volume of Anion resin per vessel |  | 11 | m3
Total volume of cation resin |  | 42 | m3 | Total volume of Anion resin |  | 33 | m3
Volume of Inert Resin per Vessel |  | 1.1 | m3 | Volume of Inert Resin per Vessel |  | 1.1 | m3
Total volume of inert resin |  | 3.3 | m3 | Total volume of inert resin |  | 3.3 | m3
Cation Resin Replacement Cost |  | 892920 |  | Anion Resin Replacement Cost |  | 977130
Inert Resin Replacement Cost |  | 55000 |  | Inert Resin Replacement Cost |  | 55000
Total resin replacement cost |  | 947920 |  | Total resin replacement cost |  | 1032130
Frequency of resin replacement |  | 7 | years | Frequency of resin replacement |  | 5 | years
Cation resin inlet flow per vessel |  | 170 | m3/h | Anion resin inlet flow per vessel |  | 170 | m3/h
Normal plant flow |  | 340 | m3/h | Normal plant flow |  | 340 | m3/h
Maximum plant flow capability |  | 510 | m3/h | Maximum plant flow capability |  | 510 | m3/h
Cation Bed Service run |  | 24 | hours | Anion Bed Service run |  | 24 | hours
Frequency of regeneration |  | 2 | per day | Frequency of regeneration |  | 2 | per day
Ionic Load Removed per Service Run |  | 11095 | as eq | Ionic Load Removed per Service Run |  | 5912 | as eq
|  | 554.75 | as kg CaCO3 |  |  | 295.6 | as kg CaCO3
Annual top-up Cation resin volume |  | 2.712 | m3 | Annual top-up Anion resin volume |  | 3.505 | m3
Annual top-up resin cost |  | 57657.12 |  | Annual top-up resin cost |  | 103783.05
Scenario 2:
Mokolo Water Supply Only: Ion Exchange-Based System - Conventional Primary Exchangers and Polishing Mixed Beds Configuration : Raw → UF → Cation (SAC) → Vacuum Degasser → Anion (SBA) → MBIX → GTM → NRMB
Mixed Bed (regenerable) Data : SAC/SBA - Amberjet 1500 H/ Ambersep 900 OH |  |  |  | IX Miscellaneous :
Number of Trains |  | 3 |  | Raw Water Usage for demin production | 2680560 | m3 per annum
Number of Vessels per train |  | 1 |  | Annualised Raw Water cost | 7430512.32
Total Number of MBIX vessels |  | 3 |  | Volume of effluent produced | 241746 | m3 per annum
Volume of SAC Cation Resin per vessel |  | 14 | m3 | Effluent solids loading per annum from Cations | 7289415 | equivalents
Total volume of SAC Cation Resin |  | 42 | m3 |  | 364.4708 | tonnes as CaCO3
Volume of SBA Anion Resin per vessel |  | 11 | m3 | Effluent solids loading p.a. from Anions | 3884184 | equivalents
Total volume of SBA Anion Resin |  | 33 | m3 |  | 194.2092 | tonnes as CaCO3
Volume of Inert Resin per Vessel |  | 1.1 | m3 | Effluent solids loading p.a. from MB Cations | 38270.25 | equivalents
Total volume of Inert Resin |  | 3.3 | m3 |  | 1.9135 | tonnes as CaCO3
Cation Resin Replacement Cost |  | 892920 |  | Effluent solids loading p.a. from MB Anions | 3668.25 | equivalents
Anion Resin Replacement Cost |  | 1407780 |  |  | 0.18341 | tonnes as CaCO3
Inert Resin Replacement Cost |  | 55000 |  | Effluent solids loading p.a. from Cation Regens | 3972838.7755 | equivalents
Total resin replacement cost |  | 2355700 |  |  | 198.6419 | tonnes as CaCO3
Frequency of resin replacement |  | 5 | years | Effluent solids loading p.a. from Anion Regens | 4344412.5 | equivalents
Cation resin flow per vessel |  | 170 | m3/h |  | 217.2206 | tonnes as CaCO3
Normal flow |  | 340 | m3/h | Effluent solids loading p.a. from MB Cation Regens | 355875 | equivalents
Maximum flow capability |  | 510 | m3/h |  | 17.7937 | tonnes as CaCO3
MBIX Service run |  | 288 | hours | Effluent solids loading p.a. from MB Anion regens | 607725 | equivalents
Frequency of regeneration |  | 0.16667 | per day |  | 30.3863 | tonnes as CaCO3
Ionic Load Removed per Service Run - MB Cation |  | 699 | as eq | Effluent solids loading p.a. from Neutralisations | 371573.7245 | equivalents
|  | 34.95 | as kg CaCO3 |  | 18.5787 | tonnes as CaCO3
Ionic Load Removed per Service Run - MB Anion |  | 67 | as eq | Total IX Effluent solids loading p.a. | 20867962.5 | equivalents
|  | 3.35 | as kg CaCO3 |  | 1043.3981 | tonnes as CaCO3
Annual top-up Cation resin volume |  | 2.712 | m3 | IX Power Usage | 2828750 | kWh per annum
Annual top-up resin cost |  | 57657.12 |  | Annualised IX Power Costs | 1595415
Annual top-up Anion resin volume |  | 3.505 | m3
Annual top-up resin cost |  | 103783.05
Chemical usage : |  |  |  | Gas Transfer Membrane (GTM) Contactor Data :
SAC Cation Regeneration |  | 840 | kg as 100% H2SO4 | Flow through GTM | 320 | m3/h
SBA Anion Regeneration |  | 501 | kg as 100% NaOH | Number of Skids (parallel operation) | 6
SAC Cation Cost per Regeneration |  | 462 |  | GTM Contactors per skid (series operation) | 4
SBA Anion Cost per regeneration |  | 869.235 |  | Total number of contactors | 24
Annualised Acid Regenerant Cost for Cations |  | 303534 |  | Frequency of GTM replacement | 7 | years
Annualised Caustic Regenerant Cost for Anions |  | 571087.395 |  | Cost of GTM Replacement | 4419000
Excess Acid per Cation Regeneration |  | 296.3 | kg as 100% H2SO4 | Nitrogen sweep rate | 7.5 | Nm3/h
|  | 6046.9388 | eq as SO42- | Nitrogen usage per annum | 69379200 | Nm3
Excess Caustic per Anion Regeneration |  | 264.5 | kg as 100% NaOH | Annualised usage @ 1.1455 kg/m3 @ NTP | 60566739.4151 | kg
|  | 6612.5 | eq as Na+ | Annualised N2 costs | 484533915.3208
Additional Acid/Caustic for neutralisation per regeneration |  | 565.5612 | eq SO4 | Power requirement for GTM | 189 | kW
MB Cation Regeneration |  | 318.5 | kg as 100% H2SO4 | Annualised GTM power usage | 1748355840 | kWh
MB Anion Regeneration |  | 444 | kg as 100% NaOH | Annualised GTM power costs | 986072693.76
MB Cation Cost Per Regeneration |  | 175.175
MB Anion Cost per Regeneration |  | 770.34
Annualised Acid Regenerant Cost for MB Cations |  | 9590.8312
Annualised Caustic Regenerant Cost for MB Anions |  | 42176.115
Excess Acid per MB Cation Regeneration |  | 318.5 | kg as 100% H2SO4
|  | 6500 | eq as SO42-
Excess Caustic per MB Anion Regeneration |  | 444 | kg as 100% NaOH
|  | 11100 | eq as Na+

## WTP-Cost-Mok
Cost of Membrane-based RO option = |  | 248820813.927 | Effluents: | IX | Solids loading | 20867962.5 | equivalents
Cost of Ion exchange-based IX option = |  | 586729735.6281 |  |  |  | 1043.3981 | tonnes as CaCO3
Absolute Difference |  | 337908921.7011 |  | RO | Solids loading | 10978485.1615 | equivalents
Mokolo supply: Weighted Mean Difference IX vs RO = |  | 40.44% |  |  |  | 548.9243 | tonnes as CaCO3
Initial capital cost : | IX = | 86737500 | Capital Cost : Absolute Difference |  |  | 1562500
| RO = | 88300000 | Capital Cost : Weighted Mean Difference = |  |  | 0.8927%
FOM (avg) | RO = | 4710234.9647

## WTP-Cost-Mix
Cost of Membrane-based RO option = |  | 316910654.9271 | Effluents: | IX | Solids loading | 100317658.5 | equivalents
Cost of Ion exchange-based IX option = |  | 1198383289.5154 |  |  |  | 5015.8829 | tonnes as CaCO3
Absolute Difference |  | 881472634.5883 |  | RO | Solids loading | 54504032.6769 | equivalents
50:50 Mixed Supply: Weighted Mean Difference IX vs RO = |  | 58.17% |  |  |  | 2725.2016 | tonnes as CaCO3
Initial capital cost : | IX = | 230487500 | Capital Cost : Absolute Difference |  |  | 109187500
| RO = | 121300000 | Capital Cost : Weighted Mean Difference = |  |  | 31.04%

## WTP-Cost-Croc
Cost of Membrane-based RO option = |  |  | 360069918.5773 |  | Effluents: | IX | Solids loading | 308873110.5 | equivalents
Cost of Ion exchange-based IX option = |  |  | 2175690645.1646 |  |  |  |  | 15443.6555 | tonnes as CaCO3
Absolute Difference |  |  | 1815620726.5873 |  |  | RO | Solids loading | 113715177.2308 | equivalents
Crocodile West Supply: Weighted Mean Difference IX vs RO = |  |  | 71.6% |  |  |  |  | 5685.7589 | tonnes as CaCO3
Initial capital cost : |  | IX = | 412862500 |  | Capital Cost : Absolute Difference |  |  | 258562500
|  | RO = | 154300000 |  | Capital Cost : Weighted Mean Difference = |  |  | 45.59%
| Mok-difference | RO = | 79200000
FOM (avg) |  | RO = | 0.45573 | 2010mZAR/Mm3
Capital as an annualised FOM |  | RO = | 2.9626 | 2010mZAR/Mm3

## Sheet2
Medupi PS : Evaporator Crystalliser Life Cycle Cost Analysis
Results
NPV this Scenario |  |  | 324578160.5898
Manpower: |  |  |  |  | Evaporator Crystalliser Data | [5 empty] | IX Anion Data : SBA - Amberjet 4200 Cl | [5 empty] | Mixed Bed (regenerable) Data : SAC/SBA - Amberjet 1500 H/ Ambersep 900 OH | [5 empty] | Chemical usage : | [5 empty] | IX Miscellaneous : |  |  |  |  | UF Plant Data : |  |  |  |  | Gas Transfer Membrane (GTM) Contactor Data : |  |  | Non-Regenerable Mixed Bed Ion Exchange (NR-MBIX) Data :
Number of Chemist/Operators for WTP per shift |  | 2 |  |  | Number of Trains |  |  | 1 |  |  | Number of Trains |  |  | 31 |  |  | Number of Trains |  |  | 3 |  |  | SAC Cation Regeneration |  |  | 840 | kg as 100% H2SO4 |  | Raw Water Usage for demin production |  | 43723574667.72 | m3 per annum |  | Flow to UF plant |  | 255.5 | m3/h |  | Flow through GTM | 320 | m3/h | Cation Resin Volume | 5 | m3
Number of Shifts per day |  | 3 |  |  | Number of Evap/Xstal per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | Number of Vessels per train |  |  | 1 |  |  | SBA Anion Regeneration |  |  | 501 | kg as 100% NaOH |  | Annualised Raw Water cost |  | 121201748978.92 |  |  | Number of UF pressure vessels housings |  | 48 |  |  | Number of Skids (parallel operation) | 6 |  | Anion Resin Volume | 5 | m3
Duration of shift |  | 9 | hours |  | Total number of Evap/Xstal |  |  | 1 |  |  | Total Number of Anion vessels |  |  | 31 |  |  | Total Number of MBIX vessels |  |  | 3 |  |  | SAC Cation Cost per Regeneration |  |  | 462 |  |  | Volume of effluent produced |  | 241746 | m3 per annum |  | Number of UF elements per housing |  | 4 |  |  | GTM Contactors per skid (series operation) | 4 |  | Resin Replacement Frequency | 2 | years
Average time spent per shift on demin plant |  | 4 | hours |  | Capital Cost of Evap/Xstal |  |  | 80000000 |  |  | Volume of Anion resin per vessel |  |  | 11 | m3 |  | Volume of SAC Cation Resin per vessel |  |  | 14 | m3 |  | SBA Anion Cost per regeneration |  |  | 869.235 |  |  | Effluent solids loading per annum from Cations |  | 113332500000 | equivalents |  | Total number of UF elements |  | 192 |  |  | Total number of contactors | 24 |  | Cation Resin Replacement Cost | 106300
Fraction of shift time spent on demin plant (average) |  | 44.44% |  |  | Flow through Evap/Xstal |  |  | 71 | m3/h |  | Total volume of Anion resin |  |  | 341 | m3 |  | Total volume of SAC Cation Resin |  |  | 42 | m3 |  | Annualised Acid Regenerant Cost for Cations |  |  | 758835000000 |  |  |  |  | 5666625 | tonnes as CaCO3 |  | UF Element replacement Cost |  | 6652800 |  |  | Frequency of GTM replacement | 7 | years | Anion Resin Replacement Cost | 213300
Number of days per annum |  | 365 | days |  | Volume treated per annum |  |  | 559764 | m3 |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  | Volume of SBA Anion Resin per vessel |  |  | 11 | m3 |  | Annualised Caustic Regenerant Cost for Anions |  |  | 8851854.6225 |  |  | Effluent solids loading p.a. from Anions |  | 60204852 | equivalents |  | UF element replacement frequency |  | 5 | years |  | Cost of GTM Replacement | 4419000
Plant availability |  | 90% |  |  | Power Requirements for Evap Section |  |  | 23.8 | kWh/m3 |  | Total volume of inert resin |  |  | 34.1 | m3 |  | Total volume of SBA Anion Resin |  |  | 33 | m3 |  | Excess Acid per Cation Regeneration |  |  | 296.3 | kg as 100% H2SO4 |  |  |  | 3010.2426 | tonnes as CaCO3 |  | UF system Recovery |  | 92.9 | % |  | Nitrogen sweep rate | 7.5 | Nm3/h
Number of operating days |  | 328.5 | days |  | Power Requirements for Xstal Section |  |  | 66.05 | kWh/m3 |  | Anion Resin Replacement Cost |  |  | 10097010 |  |  | Volume of Inert Resin per Vessel |  |  | 1.1 | m3 |  |  |  |  | 6046.9388 | eq as SO42- |  | Effluent solids loading p.a. from MB Cations |  | 38270.25 | equivalents |  | UF System Backwash water |  | 18.1405 | m3/h |  | Nitrogen usage per annum | 59130 | Nm3
Numer of operating Hours |  | 7884 |  |  | Annualised Power Requirements Evap Section |  |  | 13322383.2 | kWh |  | Inert Resin Replacement Cost |  |  | 55000 |  |  | Total volume of Inert Resin |  |  | 3.3 | m3 |  | Excess Caustic per Anion Regeneration |  |  | 264.5 | kg as 100% NaOH |  |  |  | 1.9135 | tonnes as CaCO3 |  | Annualised Backwash replacement water cost |  | 396450.6139 |  |  | Annualised usage @ 1.1455 kg/m3 @ NTP | 51619.3802 | kg
Number of manhours per annum on demin plant |  | 3504 | hours |  | Annualised Power requirements Xstal Section |  |  | 36972412.2 | kWh |  | Total resin replacement cost |  |  | 10152010 |  |  | Cation Resin Replacement Cost |  |  | 1509460 | [5 empty] | 6612.5 | eq as Na+ |  | Effluent solids loading p.a. from MB Anions |  | 3668.25 | equivalents |  | UF Power Requirement |  | 0.2 | kWh/m3 |  | Annualised N2 costs | 412955.0415
Annualised Labour Cost |  | 770880 |  |  | Works Power Cost |  |  | 0.15 | per kWh |  | Frequency of resin replacement |  |  | 5 | years |  | Anion Resin Replacement Cost |  |  | 14547060 |  |  | Additional Acid/Caustic for neutralisation per regeneration |  |  | 565.5612 | eq SO4 |  |  |  | 0.18341 | tonnes as CaCO3 |  | Annualised UF Power Usage |  | 402872.4 | kWh |  | Power requirement for GTM | 189 | kW
[5 empty] | Annualised Evap Power Cost |  |  | 1998357.48 |  |  | Anion resin inlet flow per vessel |  |  | 170 | m3/h |  | Inert Resin Replacement Cost |  |  | 27988200000 |  |  | MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from Cation Regens |  | 9.9321e+12 | equivalents |  | Annualised UF Power Cost |  | 227220.0336 |  |  | Annualised GTM power usage | 1490076 | kWh
[5 empty] | Annualised Xstal Power Cost |  |  | 5545861.83 |  |  | Normal plant flow |  |  | 340 | m3/h |  | Total resin replacement cost |  |  | 28004256520 |  |  | MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  |  |  | 496604846.9388 | tonnes as CaCO3 |  | CEB Sodium hypochlorite usage |  | 3.32 | L/d |  | Annualised GTM power costs | 840402.864
[5 empty] | Area required for Solids Disposal |  |  | 5 | ha |  | Maximum plant flow capability |  |  | 510 | m3/h |  | Frequency of resin replacement |  |  | 5 | years |  | MB Cation Cost Per Regeneration |  |  | 175.175 |  |  | Effluent solids loading p.a. from Anion Regens |  | 67338393.75 | equivalents |  |  |  | 1090.62 | L per annum
[5 empty] | Cost of liner |  |  | 100 | per m2 |  | Anion Bed Service run |  |  | 24 | hours |  | Cation resin flow per vessel |  |  | 170 | m3/h |  | MB Anion Cost per Regeneration |  |  | 770.34 |  |  |  |  | 3366.9197 | tonnes as CaCO3 |  | Annualised CEB NaOCl cost |  | 14897.8692
[5 empty] | Capital cost for solids disposal area |  |  | 5000000 |  |  | Frequency of regeneration |  |  | 31 | per day |  | Normal flow |  |  | 340 | m3/h |  | Annualised Acid Regenerant Cost for MB Cations |  |  | 9590.8312 |  |  | Effluent solids loading p.a. from MB Cation Regens |  | 355875 | equivalents |  | CEB Hydrochloric Acid usage |  | 3.97 | L/d
[5 empty] | Raw Water usage savings per hour |  |  | 69 | m3/h |  | Ionic Load Removed per Service Run |  |  | 5912 | as eq |  | Maximum flow capability |  |  | 510 | m3/h |  | Annualised Caustic Regenerant Cost for MB Anions |  |  | 42176.115 |  |  |  |  | 17.7937 | tonnes as CaCO3 |  |  |  | 1304.145 | L per annum
[5 empty] | Annualised raw water usage savings |  |  | 543996 | m3 |  |  |  |  | 295.6 | as kg CaCO3 |  | MBIX Service run |  |  | 288 | hours |  | Excess Acid per MB Cation Regeneration |  |  | 318.5 | kg as 100% H2SO4 |  | Effluent solids loading p.a. from MB Anion regens |  | 607725 | equivalents |  | Annualised CEB HCl cost |  | 930.2901
[5 empty] | Cost of Raw Water |  |  | 2.77 | per m3 |  | Annual top-up Anion resin volume |  |  | 35.751 | m3 |  | Frequency of regeneration |  |  | 0.16667 | per day |  |  |  |  | 6500 | eq as SO42- |  |  |  | 30.3863 | tonnes as CaCO3
[5 empty] | Anualised Raw Water Cost savings |  |  | 1506868.92 |  |  | Annual top-up resin cost |  |  | 1058587.11 |  |  | Ionic Load Removed per Service Run - MB Cation |  |  | 699 | as eq |  | Excess Caustic per MB Anion Regeneration |  |  | 444 | kg as 100% NaOH |  | Effluent solids loading p.a. from Neutralisations |  | 928934311224.489 | equivalents
[20 empty] | 34.95 | as kg CaCO3 |  |  |  |  | 11100 | eq as Na+ |  |  |  | 46446715.5612 | tonnes as CaCO3
[17 empty] | Ionic Load Removed per Service Run - MB Anion |  |  | 67 | as eq | [7 empty] | Total IX Effluent solids loading p.a. |  | 1.0974e+13 | equivalents
[20 empty] | 3.35 | as kg CaCO3 | [9 empty] | 548724614.9392 | tonnes as CaCO3
[17 empty] | Annual top-up Cation resin volume |  |  | 2.712 | m3 | [7 empty] | IX Power Usage |  | 28853250 | kWh per annum
[17 empty] | Annual top-up resin cost |  |  | 58890.2 | [8 empty] | Annualised IX Power Costs |  | 16273233
[17 empty] | Annual top-up Anion resin volume |  |  | 3.505 | m3
[17 empty] | Annual top-up resin cost |  |  | 1058587.11
Events/Activities |  |  | Year
Number | Description |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
1 | Capital cost of Evaporator/Crystalliser |  | 80000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Capital Cost of Solids Disposal |  | 5000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Annualised Cost of Evaporator Power |  | 999178.74 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48 | 1998357.48
4 | Annualised Cost of Crystalliser Power |  | 2772930.915 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83 | 5545861.83
5 | Annualised Cost Saving on Raw Water |  | -753434.46 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92 | -1506868.92
6 | Annualised Labour Cost |  | 385440 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880 | 770880
| Total |  | 88404115.195 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39 | 6808230.39
| Index |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
| Escalation |  | 102447307.803 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106 | 7889733.106
| Discount |  | 87832054.0149 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736 | 6764174.4736
| Actual Net Present Value |  | 87832054.0149 | 94596228.4885 | 101360402.962 | 108124577.4356 | 114888751.9092 | 121652926.3827 | 128417100.8563 | 135181275.3299 | 141945449.8034 | 148709624.277 | 155473798.7506 | 162237973.2242 | 169002147.6977 | 175766322.1713 | 182530496.6449 | 189294671.1184 | 196058845.592 | 202823020.0656 | 209587194.5391 | 216351369.0127 | 223115543.4863 | 229879717.9598 | 236643892.4334 | 243408066.907 | 250172241.3805 | 256936415.8541 | 263700590.3277 | 270464764.8012 | 277228939.2748 | 283993113.7484 | 290757288.2219 | 297521462.6955 | 304285637.1691 | 311049811.6427 | 317813986.1162 | 324578160.5898
| Actual Net Present Value ( x R 1000) |  | 87832.054 | 94596.2285 | 101360.403 | 108124.5774 | 114888.7519 | 121652.9264 | 128417.1009 | 135181.2753 | 141945.4498 | 148709.6243 | 155473.7988 | 162237.9732 | 169002.1477 | 175766.3222 | 182530.4966 | 189294.6711 | 196058.8456 | 202823.0201 | 209587.1945 | 216351.369 | 223115.5435 | 229879.718 | 236643.8924 | 243408.0669 | 250172.2414 | 256936.4159 | 263700.5903 | 270464.7648 | 277228.9393 | 283993.1137 | 290757.2882 | 297521.4627 | 304285.6372 | 311049.8116 | 317813.9861 | 324578.1606

## Sheet1
Capital Cost of Evaporator /Crystalliser = | 80000000
Capital Cost of Solid Waste Disposal = | 5000000
Volume of Raw Water Saved per annum = | 543996 | m3