## existing
Historical Reservoir and Hydropower Data | Value | units | Sources | Comment
Mozambique - plants with reservoirs
Cahora Bassa | [5 empty] | Turbine efficency
Owner | HCB |  |  |  |  | net head (m) | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 125 | 130
Generator data | [5 empty] | efficiency | 89.3% | 92.7% | 95.8% | 95.6% | 95.6% | 95.9% | 95.6% | 95.2% | 94.2% | 92.9%
Date of commissioning (generator) | 1976-77 | year | HCB; Euroconsult Mott McDonald 2008 says 1975 |  |  | Volume Elevation curve
Average annual production | 14729 | GWh | HCB | Average 2004-2012; HCB says 15,500 in future | 0.81031 | volume (mcm) | 0 | 4745 | 10689 | 17963 | 26699 | 37026 | 51704 | 62977 | 65991
Current installed capacity | 2075 | MW | HCB; Euroconsult Mott McDonald 2008 | 5 turbines, usually only run 4 |  | elevation (m amsl) | 295 | 300 | 305 | 310 | 315 | 320 | 326 | 330 | 331 | 36
Date of major refurbishment | 2003-2006 | year |  | 1981-1998 civil war disrupted operation of reservoir |  | area (km2) | 838 | 1065 | 1317 | 1597 | 1902 | 2233 | 2665 | 2974 | 3054
Installed capacity prior to refurbishment | 2075 | MW |  |  |  | spillway (cms) | 6760 | 7990 | 9060 | 10020 | 10890 | 11700 | 12600 | 14173 | 15683
Availability (net of planned and forced outages) | 96% | % | HCB | After refurbishement , average from 2008 up to 2011 |  | Source: HCB; Beilfuss
Generating efficiency | 95.6 | % | based on average flow, tailwater rating and average storage level |  |  | Design Flood Rule Curve (end of month levels) | [15 empty] | from literature
Maximum turbine flow (if relevant) | 2000 | cms | to match rated capacity and pers comm Gaule ( note HCB reports 2520 and Beilfuss 2001 Vol 4 Table 4-5 has 2260) |  |  | Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  |  | Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Reservoir data | [5 empty] | Level (m amsl) | 321.7 | 323.6 | 325.6 | 325.7 | 325.4 | 325.1 | 324.5 | 324 | 323.1 | 322.2 | 321.3 | 320.6 |  |  | Level (m amsl) | 321.4 | 324.7 | 328.4 | 329 | 329 | 328 | 326 | 326 | 326 | 326 | 323 | 320.8
Date of commissioning (reservoir) | 1975 | year | HCB | commissioned in 1974, operational in model in 1975 |  | volume (mcm) | 41184.7667 | 45832.8 | 50576.7 | 50858.525 | 50013.05 | 49167.575 | 40206.2333 | 40206.2333 | 40206.2333 | 40206.2333 | 40206.2333 | 38493.8 | calculated from volume elevation curve |  |  | -0.3 | 1.1 | 2.8 | 3.3 | 3.6 | 2.9 | 1.5 | 2 | 2.9 | 3.8 | 1.7 | 0.2
Reservoir storage capacity | 65000 | mcm | HCB; Beilfuss 2001 Vol 4 Table 4-5; Yamba et al has 63,000 |  |  | Design Flood Rule Curve (end of month levels) Month: Source: Kling/ZDSS based on observation in 2000s (differs from Beilfuss)
Surface area | 2665 | km2 | HCB; Beilfuss 2001 Vol 4 Table 4-5; Yamba et al has 2660 | at 326 m |  | Design Flood Rule Curve (end of month levels) Month: Operating Zones (mcm)
Volume-elevation curve | see table |  | HCB; Beilfuss 2001 Vol 4 Table 4-5 |  |  | Design Flood Rule Curve (end of month levels) Month: Top of Storage; Design Flood Rule Curve (end of month levels) Jan: 65991
Maximum hydraulic flow | 16250 | cms | Beilfuss 2001 Vol 2 p22 |  |  | Top of Conservation | 41184.7667 | 45832.8 | 50576.7 | 50858.525 | 50013.05 | 49167.575 | 40206.2333 | 40206.2333 | 40206.2333 | 40206.2333 | 40206.2333 | 38493.8
Reservoir elevation when full | 326 | m | HCB; Beilfuss 2001 Vol 4 Table 4-5 | top of conservation |  | Design Flood Rule Curve (end of month levels) Month: Top of Buffer; Design Flood Rule Curve (end of month levels) Jan: 0 | no distinction made for buffer zone
Reservoir net evaporation (net of rainfall) | see table | mm/mo | Beilfuss 2001 WP2 Table 2-16/ HMN 2012 Report |  |  | Design Flood Rule Curve (end of month levels) Month: Top of Inactive; Design Flood Rule Curve (end of month levels) Jan: 0
Operating zones (top of conservation, buffer, inactive) | see table | % or mcm | HCB; Beilfuss 2001 Vol 4 Table 4-5 | based on Design Flood Rule Curve |  | Tailwater rating curve | 197.17 | 198.7084 | 200.2132 | 203.1221 | 205.8965 | 211.0424 | 217.7534 | 222.4221 | 228.7095 | 233.0814
Tailwater elevation | 202 | m | HCB; Beilfuss 2001 Vol 4 Table 4-5; Yamba et al report head as 103.5m |  |  | Discharge (cms) | 0 | 500 | 1000 | 2000 | 3000 | 5000 | 8000 | 10500 | 15000 | 22000
Time series data (to be supplied in spreadsheets) | [5 empty] | Discharge (mcm) | 0 | 1296 | 2592 | 5184 | 7776 | 12960 | 20736 | 27216 | 38880 | 57024
Monthly historical production (1960-2012) |  | GWh | HCB | in separate file |  | Level (m amsl) | 193.98 | 198.89 | 201.08 | 204.29 | 206.86 | 211.05 | 216.05 | 221.5 | 226.14 | 232 | Source: HCB; Beilfuss 2001 vol 4
Observed volume or resevoir height (1960-2012) |  | m | HCB | in separate file |  | Historical net evaporation (mm) |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Source
Qualitative data | [5 empty] | Evaporation |  | 176 | 146 | 169 | 156 | 147 | 128 | 142 | 190 | 245 | 281 | 234 | 185 | Beilfuss 2001 WP2 Table 2-16/ HMN 2012 Report
Operating guidelines | see Design Rule Flood Curve |  |  |  |  | Rainfall |  | 169 | 145 | 97 | 20 | 7 | 4 | 2 | 1 | 0 | 7 | 49 | 145
[6 empty] | Net evaporation | Beilfuss | 7 | 1 | 72 | 136 | 140 | 124 | 140 | 189 | 245 | 274 | 185 | 40
[6 empty] | Net evaporation | HCB | 44 | 16 | 95 | 137 | 139 | 118 | 119 | 164 | 218 | 269 | 181 | 62
[6 empty] | Net evaporation | WEAP | -33.6711 | -30.8757 | 23.9538 | 101.9457 | 114.0469 | 99.9171 | 106.905 | 137.9645 | 178.5953 | 195.955 | 122.4686 | -29.2852 | WEAP
Zambia plants + Kariba South (Zim) | still need LHPC
Kariba North
Owner | ZESCO
Date of commissioning (generator) | 1959 | year | Beilfuss & Brown 2010 |  | 238.25 | Design Flood Rule Curve (end of month levels) Month: friction head loss; Design Flood Rule Curve (end of month levels) Jan: 0.7; Design Flood Rule Curve (end of month levels) Feb: m; Design Flood Rule Curve (end of month levels) Mar: Beilfuss 2001 Vol 4 Table 4-1
Average annual production | 2859 | GWh | ZESCO | Average 1993-2012 | 45.33%
Current installed capacity | 720 | MW | MEWD (2010) Zambia Power Development Master Plan |  |  | Design Flood Rule Curve (end of month levels) Month: Volume Elevation curve; Design Flood Rule Curve (end of month levels) Jan: Min |  | Max |  |  | 600 | MW | Yamba et al book
Date of major refurbishment | N/A | year |  | if plant was upgraded |  | volume (mcm) | 54 | 2272 | 6706 | 11278 | 15911 | 20613 | 25962 | 30408 | 35427 | 40568 | 45778 | 51088 | 56507 | 64798 | 76854
Installed capacity prior to refurbishment | N/A | MW |  |  |  | elevation (m amsl) | 475.5 | 476 | 477 | 478 | 479 | 480 | 481 | 482 | 483 | 484 | 485 | 486 | 487 | 488.5 | 489.5
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 |  |  | area (km2) | 4354 | 4405 | 4507 | 4608 | 4709 | 4811 | 4901 | 4991 | 5081 | 5171 | 5261 | 5350 | 5440 | 5577 | 5671
Generating efficiency | 88% | % | Beilfuss 2001 Vol 4 Table 4-1 |  |  | spillway (cms) |  |  |  |  | 7528 | 7751 | 7973 | 8168 | 8381 | 8584 | 8786 | 8974 | 9161 | 9445 | 9515
Maximum turbine flow (if relevant) | 878.6939 | cms | estimated from 1794 cms total for Kariba dam in WB Model
Date of commissioning (reservoir) | 1959 | year | Beilfuss & Brown 2010 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005
Reservoir storage capacity | 64798 | mcm | Beilfuss 2001 Vol 4 Table 4-1 |  |  | Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Surface area | 5577 | km2 | Beilfuss 2001 Vol 4 Table 4-1 |  |  | Level (m amsl) | 485.15 | 484.15 | 485.7 | 487.5 | 487.5 | 487.5 | 487.5 | 487.5 | 487 | 486.5 | 486 | 485.5 | calculated from volume elevation curve
Volume-elevation curve | see table |  | Beilfuss Table and Yamba et al from ZRA |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: volume (109 m3)
Maximum hydraulic flow | 9515 | cms | Beilfuss 2010; Yamba et al book says 9500 | for both power plants (North and South) |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Source: ZRA pers comm, Dam Synchronisation Study Annex 2 p72
Reservoir elevation when full | 488.5 | m | Beilfuss 2001 Vol 4 Table 4-1 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Operating Zones (m amsl)
Reservoir net evaporation (net of rainfall) |  | mm/mo |  |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Storage
Operating zones (top of conservation, buffer, inactive) | see table | % or mcm | Beilfuss 2001 Vol 4 Table 4-1 |  |  | Top of Conservation | 485.15 | 484.15 | 485.7 | 487.5 | 487.5 | 487.5 | 487.5 | 487.5 | 487 | 486.5 | 486 | 485.5
Tailwater elevation | 384-405 | m | Beilfuss 2001 Vol 4 Table 4-1 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Buffer; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 0 | no distinction made for buffer zone
Time series data (to be supplied in spreadsheets) | [5 empty] | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Inactive
Monthly historical production (1960-2012) | separate sheet | GWh | ZESCO | received from ZESCO for 1993-2012 |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Tailwater rating curve
Observed volume or resevoir height (1960-2012) |  | m |  |  |  | Discharge (cms) | 0 | 479 | 719 | 959 | 1319 | 1518 | 3000 | 9000 | 12000 | 15000
Qualitative data | [5 empty] | Level (m amsl) | 379.95 | 383.7 | 384.86 | 386.19 | 387.67 | 388.48 | 391.96 | 399.87 | 402.55 | 404.55
Operating guidelines | see Design Flood Rule Curve |  | Beilfuss 2001 Vol 4 Table 4-1
Kariba South - Zimbabwe
Owner | ZESA |  |  |  | 6443
Date of commissioning (generator) | 1958 | year | Euroconsult Mott McDonald 2007
Average annual production | 3584 | GWh | IEA | Average 1993-2012 | 54.74%
Current installed capacity | 750 | MW | Burian et al 2012 SAPP Grid Emissions Factor
Date of major refurbishment | N/A | year |  | if plant was upgraded
Installed capacity prior to refurbishment | N/A | MW
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 | this is availability and not load factor
Generating efficiency | 88% | % | Beilfuss 2001 Vol 4 Table 4-1
Maximum turbine flow (if relevant) | 915.3061 | cms | estimated from 1794 cms total for Kariba dam in WB Model
Kafue Gorge Upper | [5 empty] | Design Flood Rule Curve (end of month levels) - revised 2005 Month: friction head loss; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 1; Design Flood Rule Curve (end of month levels) - revised 2005 Feb: m
Owner | ZESCO |  |  |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Volume Elevation curve; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: Min
Date of commissioning (generator) | 1968 | year | Burian et al 2012 SAPP Grid Emissions Factor |  | 430 | volume (mcm) | 0 | 20 | 69 | 170 | 423 | 785 | 1178 | 2845
Average annual production | 5160 | GWh | ZESCO | Average 1993-2012 | 0.59499 | elevation (m amsl) | 972.3 | 973 | 974 | 975 | 976 | 976.6 | 977 | 978
Current installed capacity | 990 | MW | MEWD (2010) Zambia Power Development Master Plan |  |  | area (km2) | 20 | 35 | 70 | 142 | 430 | 805 | 1175 | 2160
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 |  |  | spillway (cms) | 780 | 1076 | 1420 | 1804 | 2220 | 2496 | 2668 | 3132
Generating efficiency | 88% | % | Beilfuss 2001 Vol 4 Table 4-4
Maximum turbine flow | 252 | cms | Beilfuss 2001 Vol 2 p18
Time series data (to be supplied in spreadsheets)
Date of commissioning (reservoir) | 1968 | year | as above |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Operating Zones (mcm)
Reservoir storage capacity | 785 | mcm | Beilfuss 2001 Vol 4 Table 4-4 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Storage; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 785
Surface area | 805 | km2 | Beilfuss 2001 Vol 4 Table 4-4 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Conservation
Volume-elevation curve | see table |  | Beilfuss 2001 Vol 4 Table 4-4 |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Buffer; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 0
Maximum hydraulic flow | N/A | cms |  |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Top of Inactive; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 0
Reservoir elevation when full | 976.6 | m | Beilfuss 2001 Vol 4 Table 4-4
Reservoir net evaporation (net of rainfall) |  | mm/mo
Operating zones (top of conservation, buffer, inactive) | 100 | % or mcm | Beilfuss 2001 Vol 4 Table 4-4 | no buffer zone or inactive zone
Tailwater elevation | 581.9 | m | Beilfuss 2001 Vol 4 Table 4-4
Time series data (to be supplied in spreadsheets)
Monthly historical production (1960-2012) | separate sheet | GWh | ZESCO | received from ZESCO for 1993-2012
Observed volume or resevoir height (1960-2012) |  | m
Qualitative data
Operating guidelines (i.e. how decisions to release are made) | none provided
Victoria Falls
Owner | ZESCO
Date of commissioning (generator) | 1972 | year | MEWD (2010) Zambia Power Development Master Plan
Average annual production | 612 | GWh | ZESCO | Average 1993-2012 | 64.69%
Current installed capacity | 108 | MW | MEWD (2010) Zambia Power Development Master Plan
Date of major refurbishment | 1968 | year | MEWD (2010) Zambia Power Development Master Plan
Installed capacity prior to refurbishment | 68 | MW | MEWD (2010) Zambia Power Development Master Plan
Availability (net of planned and forced outages) | 93% | % | Nexant 2007
Generating efficiency | 88% | % | assumed to be same as Kariba
Maximum turbine flow | 117.2 | cms | MEWD (2010) Zambia Power Development Master Plan
Fixed head height | 112.7 | m | MEWD (2010) Zambia Power Development Master Plan
Monthly historical production (1960-2012) | separate sheet | GWh | ZESCO | received from ZESCO for 1993-2012
Lunsemfwa
Owner | LHPC
Date of commissioning (generator) | 1944 | year | Euroconsult Mott McD 2007
Average annual production | 113 | GWh | Euroconsult Mott McD 2007
Current installed capacity | 18 | MW | MEWD (2010) Zambia Power Development Master Plan
Date of commissioning (reservoir) | 1944 | year
Reservoir storage capacity |  | mcm
Surface area | 45 | km2 | Euroconsult Mott McD 2007
Reservoir elevation when full |  | m
Net Head | 380 | m | Euroconsult Mott McD 2007
Mulungushi
Owner | LHPC
Date of commissioning (generator) | 1955 | year | Burian et al 2012 SAPP Grid Emissions Factor
Average annual production | 80 | GWh | Euroconsult Mott McD 2007
Current installed capacity | 20 | MW | MEWD (2010) Zambia Power Development Master Plan
Reservoir storage capacity |  | mcm
Surface area | 31 | km2 | Euroconsult Mott McD 2007
Reservoir elevation when full |  | m
Net Head | 325 | m
Combined Lunsemfwa-Mulungushi for model
Owner | LHPC |  |  |  |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: scaling factor; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: 0.20321
Date of commissioning (generator) | 1944 | year |  | similar to Lunsumfwa |  | Design Flood Rule Curve (end of month levels) - revised 2005 Month: Volume Elevation curve; Design Flood Rule Curve (end of month levels) - revised 2005 Jan: Min |  | Max
Average annual production | 193 | GWh |  | combined for both |  | volume (mcm) | 142.0428 | 181.6684 | 227.3904 | 279.8182 | 339.9679 | 408.0428 | 485.0588 | 571.8289 | 668.7594 | 721.5936 | 836.8128 | 964.4278 | 1105.2513 | 1142.8449 | 1432.4171
Current installed capacity | 38 | MW |  | combined for both |  | elevation (m amsl) | 1006 | 1008 | 1010 | 1012 | 1014 | 1016 | 1018 | 1020 | 1022 | 1024 | 1026 | 1028 | 1029 | 1029.5 | 1035
Availability (net of planned and forced outages) | 93% | % |  | default from Nexant 2007 |  | area (km2) | 18.2888 | 21.3369 | 24.385 | 28.0428 | 32.107 | 35.9679 | 41.2513 | 45.5187 | 51.4118 | 57.7112 | 63.8075 | 70.3102 | 73.9679 | 76 | 90.631
Generating efficiency | 90% | % |  | default from USBR 2005 |  | All estimated from scaling Itezhi-tezhi
Reservoir storage capacity | 1142.8449 | mcm |  | scaled from Itezhi-tezhi |  | Note: Lunsemfwa and Mulungushi are also about 1100 m amsl
Surface area | 76 | km2 |  | combined for both
Volume-elevation curve | see table |  |  | scaled from Itezhi-tezhi
Reservoir elevation when full | 1029.5 | m |  | this is for model; actual is roughly at 1100m amsl
Tailwater elevation | 649.5 |  |  | calculated
Net Head | 380 | m |  | using Lunsemfwa head
Itezhi-tezhi
Owner | ZESCO/TATA
Estimated date of commissioning | 1977 | year | Beilfuss 2001 Vol 2 | 1976-12-01 |  | Volume Elevation curve | 1006: Min; 1029.5: Max
Reservoir storage capacity | 5624 | mcm | Beilfuss 2001 Vol 4 Table 4-2; Beilfuss 2010 - but use live storage for model |  |  | volume (mcm) | 699 | 894 | 1119 | 1377 | 1673 | 2008 | 2387 | 2814 | 3291 | 3551 | 4118 | 4746 | 5439 | 5624 | 7049
Surface area | 374 | km2 |  |  |  | elevation (m amsl) | 1006 | 1008 | 1010 | 1012 | 1014 | 1016 | 1018 | 1020 | 1022 | 1024 | 1026 | 1028 | 1029 | 1029.5 | 1035
Volume-elevation curve | see table |  | Beilfuss 2001 Vol 4 Table 4-2 |  |  | area (km2) | 90 | 105 | 120 | 138 | 158 | 177 | 203 | 224 | 253 | 284 | 314 | 346 | 364 | 374 | 446
Maximum hydraulic flow | not specified | cms |  |  |  | spillway (cms) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 402 | 690 | 1125 | 1674 | 2355 | 2700 | 2910 | 4450
Reservoir elevation when full | 1029.5 | m |  |  |  | Live storage | 0 | 195 | 420 | 678 | 974 | 1309 | 1688 | 2115 | 2592 | 2852 | 3419 | 4047 | 4740 | 4925 | 6350 | matches CEEEZ analysis
Reservoir net evaporation (net of rainfall) |  | mm/mo |  |  |  | Design Flood Rule Curve | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Operating zones (top of conservation, buffer, inactive) | see comment | % or mcm |  | inactive below 699 mcm/1006m |  | elevation | 1023.4551 | 1025.864 | 1027.4718 | 1028.5246 | 1028.5638 | 1028.1598 | 1027.6226 | 1026.8355 | 1025.741 | 1024.5418 | 1023.2483 | 1022.5132
Tailwater elevation | 985.8 | m |  | calculated from mean surface level and net head (CEEEZ data) |  | volume
Average head | 40 | m | Euroconsult Mott MdD 2007
Qualitative data
Operating guidelines (i.e. how decisions to release are made) | see comment |  | Beilfuss 2010 | must have 300 cms flood in month of March; but not happening often
Malawi
Nkula Falls A
Owner | ESCOM
Date of commissioning (generator) | 1966 | year | Euroconsult Mott McDonald 2007
Average annual production | 161 | GWh | Escom pers comm | average of 2005-2012
Current installed capacity | 24 | MW | Euroconsult Mott McDonald 2007 |  | 76.58%
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 | default assumption
Generating efficiency | 90% | % |  | as per USBR 2005
Maximum turbine flow | 47.6129 | cms | WB MSIOA | total Nkula Falls is 246 cms, so weighted by capacity
Fixed head height | 52 | m | Euroconsult Mott McDonald 2007 (Annex 2)
Nkula Falls B
Owner | ESCOM
Date of commissioning (generator) | 1981 | year | Euroconsult Mott McDonald 2007
Average annual production | 575 | GWh | Escom pers comm | average of 2005-2012
Current installed capacity | 100 | MW | Euroconsult Mott McDonald 2007 |  | 65.64%
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 | default assumption
Generating efficiency | 90% | % |  | as per USBR 2005
Maximum turbine flow | 198.3871 | cms | WB MSIOA | total Nkula Falls is 246 cms, so weighted by capacity
Fixed head height | 57 | m | Euroconsult Mott McDonald 2007 (Annex 2)
Tedzani I&II
Owner | ESCOM
Date of commissioning (generator) | 1977 | year | Euroconsult Mott McDonald 2007 | note that I was commissioned in 1973
Average annual production | 276 | GWh | Escom pers comm | average of 2005-2012
Current installed capacity | 40 | MW | Euroconsult Mott McDonald 2007 |  | 0.78767
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 | default assumption
Generating efficiency | 90% | % |  | as per USBR 2005
Maximum turbine flow | 119.0939 | cms | WB MSIOA | MSIOA has 276cms, so weighted by capacity
Fixed head height | 37 | m | http://www.escom.mw/station-tedzani.php | Euronconsult has same value
Tedzani III
Owner | ESCOM
Date of commissioning (generator) | 1995 | year | Euroconsult Mott McDonald 2007
Average annual production | 312 | GWh | Escom pers comm | average of 2005-2012
Current installed capacity | 52.7 | MW | Euroconsult Mott McDonald 2007 |  | 0.67583
Availability (net of planned and forced outages) | 93% | % | Nexant 2007 | default assumption
Generating efficiency | 90% | % |  | as per USBR 2005
Maximum turbine flow | 156.9061 | cms | WB MSIOA | MSIOA has 276cms, so weighted by capacity
Fixed head height | 37 | m | http://www.escom.mw/station-tedzani.php | Eurconsult has 42m
Kapichira I
Owner | ESCOM
Date of commissioning (generator) | 2000 | year | Escom website
Average annual production | 427 | GWh | Escom pers comm | average of 2005-2012 | 76.16%
Current installed capacity | 64 | MW | Euroconsult Mott McDonald 2007
Availability (net of planned and forced outages) | 91.15% | % | Nexant 2007 | actaul for this plant
Generating efficiency | 90% | % |  | as per USBR 2005
Maximum turbine flow | 134 | cms | http://www.escom.mw/station-kapichira.php | MSIOA has same value
Fixed head height | 54 | m | http://www.escom.mw/station-kapichira.php | Eurconsult has same value
Note on C1: Randall Spalding-Fecher: I deleted time slice column and just put this with units, e.g. mm/mo

## future
Future Reservoir and Hydropower Data | Value | Units | Source | Comment |  | Data Tables | [5 empty] | Other data | Source
Mozambique
Mphanda Nkuwa
Owner | Government of Mozambique
Generator data | Value | Units | Source | Comment
Esimated date of commissioning | 2018 | year | HMNK
Estimated annual production | 8600 | GWh | HMNK | net of own consumption and step up loss | 0.65449 | Area (km2) | 3.7 | 6.4 | 9.7 | 13.3 | 16.7 | 23.8 | 31.8 | 41 | 50.6 | 61.8 | 72.7 | 84.1 | 96.5 | 109.3 | 122.7 | 136
Estimated installed capacity | 1500 | MW | HMNK | SAPP CC Aug 2012 concurs |  | Volume (mcm) | 14 | 39 | 79 | 137 | 212 | 313 | 452 | 634 | 863 | 1144 | 1480 | 1872 | 2324 | 2838 | 3418 | 4065
Estimated availability (net of planned and forced outages) | 91.3% | % | HMNK |  |  | Elevation (m) | 145 | 150 | 155 | 160 | 165 | 170 | 175 | 180 | 185 | 190 | 195 | 200 | 205 | 210 | 215 | 220
Generating efficiency | 93.6% | % | HMNK |  |  | Source: HMN 2012 Feasibility Study
Maximum turbine flow | 2730 | cms | HMNK | necessary to meet capacity rating (HMNK 622 cms) |  | Production | January | February | March | April | May | June | July | August | September | October | November | December | Total
Estimated monthly production (if it varies by month) | see table | GWh | HMNK |  |  | GWh/mo | 619 | 819 | 1003 | 969 | 900 | 614 | 619 | 619 | 600 | 619 | 600 | 619 | 8600
Reservoir data | [5 empty] | At 400kV substation
Date of commissioning (reservoir) | 2018 | year |  |  |  | Source: HMNK
Reservoir storage capacity | 2324 | mcm | HMN 2012 Feasibility Study | at 205m amsl
Surface area | 96.5 | km2 | HMN 2012 Feasibility Study | at 205m amsl
Volume-elevation curve | see table |  | HMN 2012 Feasibility Study
Maximum hydraulic flow | N/A | cms
Reservoir elevation when full | 207 | m | HMN 2012 Feasibility Study | this is top of conservation
Reservoir net evaporation (net of rainfall) | see HCB | mm/mo | HMN 2012 Feasibility Study | same as Cahora Bassa
Operating zones (top of conservation, buffer, inactive) | 205 is TOC | % or mcm | HMN 2012 Feasibility Study
Tailwater elevation | 140 | m | HMN 2012 Feasibility Study | estimate from rated head of 67m and normal top of 207m
Cahora Bassa North Bank
Owner | HCB |  |  | treated as expansion of existing plant - increase max turbine flow and demand
Generator data |  |  |  | uses existing reservoir at Cahora Bassa
Estimated date of commissioning | 2017 |  | SAPP TW2 input
Estimated annual production | 2835 | GWh | Nexant (2007) | in peak use configuration | 0.25994
Estimated installed capacity | 1245 | MW | SAPP CC report on new projects (Aug 2012)
Estimated availability (net of planned and forced outages) | 97% | % | HCB
Generating efficiency | 94% | % |  | as per HCB original
Maximum turbine flow | 1210 | cms |  | estimated to match rated capacity
Boroma
Owner
Estimated annual production | 1167.5676 | GWh | estimated from EuroConsultant Mott McDonald load factor (3240 GWh for 444MW) |  | 0.83302
Estimated installed capacity | 160 | MW | SAPP 2012 hydro; and EDM
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow | 1115 | cms |  | estimated to match rated capacity
Fixed head height | 17 | m | Euroconsult Mott McDonald (2007) | 142m amsl
Lupata
Owner
Estimated annual production | 4171.2538 | GWh | estimated from EuroConsultant Mott McDonald load factor (4960 GWh for 654 MW) |  | 0.86576
Estimated installed capacity | 550 | MW | EDM and SAPP 2012 hydro
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow | 2410 | cms |  | estimated to match rated capacity
Fixed head height | 27 | m | Euroconsult Mott McDonald (2007) | 125m amsl
Ruo
Owner | EDM
Estimated annual production |  | GWh |  |  | 0
Estimated installed capacity | 100 | MW | EDM powerpoint slide
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms
Fixed head height |  | m
Chemba
Owner |  |  |  | it appears that Chemba and Ancuaze Sinjal may be mutually exclusive
Generator data | [6 empty] | 155: surface; 160: head
Estimated annual production | 8760 | GWh |  |  | 0.96154 |  | 150: HCB; 155: est; 160: est; 165: avg
Estimated installed capacity | 1040 | MW | Euroconsult Mott McDonald 2007 |  |  |  | 145: storage; 150: 52000; 155: 27265.9176; 160: 20327.2727; 165: 23796.5952
Esatimted availability (net of planned and forced outages) | 93 | % | Nexant (2007) | default value from Nexant 2007 |  |  | 145: surface; 150: 2670
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa |  |  | 145: head; 150: 110
Maximum turbine flow (if relevant) |  | cms |  | maximum reservoir outflow due to hydraulic constraints, if appropriate |  |  | 145: res depth; 150: 36; 155: 18.8764; 160: 14.0727; 165: 13.9018
Reservoir data | [6 empty] | 155: surface est; 160: head est; 165: storage est
Projected reservoir storage capacity | 20080.3221 | mcm |  | est using GRandD database equation
Surface area | 1400 | km2 | Euroconsult Mott McDonald 2007 |  |  |  | 145: Using GRanD equation; 160: 20080.3221
Volume-elevation curve |  |  |  | reservoir depth est using HCB characteristics
Reservoir elevation when full | 98 | m | Euroconsult Mott McDonald 2007 | full supply level is 98m
Esimated reservoir net evaporation (net of rainfall) |  | mm/mo |  | 3052 mcm/yr in Euroconsult main report
Head | 43 | m | Euroconsult Mott McDonald 2007 (Annex 2) | dam height 50m
Ancuaze-Sinjal I
Owner
Estimated annual production | 2230 | GWh | Euroconsult Mott McDonald (2007) |  | 0.77141
Estimated installed capacity | 330 | MW | Euroconsult Mott McDonald (2007)
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms
Fixed head height | 13 | m |  | 98m amsl
Ancuaze-Sinjal II
Owner
Estimated annual production | 4460 | GWh | Euroconsult Mott McDonald (2007) |  | 0.84855
Estimated installed capacity | 600 | MW | Euroconsult Mott McDonald (2007)
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms
Fixed head height | 27 | m |  | 98m amsl
Luia River Hydro (7.6)
Owner
Estimated annual production | 600 | GWh | Euroconsult Mott McDonald (2007) |  | 0.25653
Estimated installed capacity | 267 | MW | Euroconsult Mott McDonald (2007)
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms |  | maximum flow possible through the turbines from design
Fixed head height | 90 | m
Capoche River Hydro (7.11)
Owner
Estimated annual production | 250 | GWh |  |  | 0.47565
Estimated installed capacity | 60 | MW | Euroconsult Mott McDonald (2007)
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms |  | maximum flow possible through the turbines from design
Fixed head height | 88 | m
Revubue River Hydopower Plants (may need more than one table)
Owner
Estimated annual production | 845 | GWh
Estimated installed capacity | 231 | MW | 231 MW over 3 plants according to Euroconsult Mott McD
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 94 | % |  | as per Mphanda Nkuwa
Maximum turbine flow |  | cms |  | maximum flow possible through the turbines from design
Fixed head height | >100 | m
Zambia
Kariba North Bank Extension
Owner | ZESCO
Esimated date of commissioning | 2013 |  | SAPP TW2 input
Estimated additional annual production | 380 | GWh | MEWD (2010)
Estimated additional installed capacity | 360 | MW | MEWD (2010) |  | 0.1205
Estimated availability (net of planned and forced outages) | 96% | % |  | to match max turbine flow to MW capacity
Generating efficiency | 88% | %
Maximum turbine flow | 455 | cms | MEWD (2010) | note that this is far more than necessary for very low production levels
Tailwater elevation |  | m |  | as per Kariba North original
Net head | 89 | m | MEWD (2010)
Itezhi-tezhi
Owner | ZESCO/TATA
Estimated date of commissioning | 2014 |  | SAPP TW2 input
Estimated annual production | 611 | GWh | MEWD (2010) |  | 58.12%
Estimated installed capacity | 120 | MW | Nexant (2007); MEWD (2010)
Estimated availability (net of planned and forced outages) | 95% | % | MEWD (2010) | plant factor is 95% so availability must be this or greater
Generating efficiency | 95% | % |  | set to match rated capacity and max flow
Maximum turbine flow | 306 | cms | MEWD (2010) | maximum flow possible through the turbines from design
Tailwater elevation | 989.5 | m amsl |  | reservoir when full less net head
Net head | 40 | m | MEWD (2010)
Kafue Gorge Lower
Owner | ZESCO
Estimated date of commissioning | 2017 |  | SAPP TW2 input
Estimated annual production | 2400 | GWh | MEWD (2010)
Estimated installed capacity | 750 | MW | MEWD (2010) |  | 0.3653
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 88% | % |  | as per Kafue Upper
Maximum turbine flow | 434 | cms | MEWD (2010) | maximum flow possible through the turbines from design
Fixed head height | 186 | m | MEWD (2010)
Kabompo Gorge
Owner | CEC |  |  | small (289 MCM) reservoir not modelled
Estimated annual production | 176 | GWh | MEWD (2010)
Estimated installed capacity | 34 | MW | MEWD (2010) |  | 0.59092
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 88% | % |  | as per Kafue Upper
Maximum turbine flow | 24 | cms | MEWD (2010)
Fixed head height | 160 | m | MEWD (2010)
Lunsumfwa Extension
Owner | LHPC
Estimated annual production | 462 | GWh | MEWD (2010)
Estimated installed capacity | 55 | MW | MEWD (2010) |  | 0.9589
Estimated availability (net of planned and forced outages) | 96 | % | MEWD (2010)
Generating efficiency | 88% | % |  | as per Kafue Upper
Maximum turbine flow | 19 | cms | MEWD (2010)
Fixed head height | 330.5 | m | MEWD (2010)
Mkushi
Owner | CEC
Estimated annual production | 223 | GWh | MEWD (2010)
Estimated installed capacity | 65 | MW | MEWD (2010) |  | 0.39164
Estimated availability (net of planned and forced outages) | 93 | % |  | default value from Nexant 2007
Generating efficiency | 88% | % |  | as per Kafue Upper
Maximum turbine flow | 21 | cms | MEWD (2010)
Fixed head height | 357 | m | MEWD (2010)
Batoka Gorge
Owner/Developer | ZRA
Estimated date of commissioning | 2018 |  | SAPP TW2 input
Estimated annual production | 8728 | GWh | ZRA | 727.3333 |  |  | 185: full
Estimated installed capacity | 1600 | MW | ZRA | 800 MW on each side (MEWD concurs) | 62.27% | Area (km2) | 1.3 | 3.8 | 5.65 | 9.22 | 12.48 | 16.15 | 20.24 | 25.07 | 30.72 | 37.31
Estimated availability (net of planned and forced outages) | 93%
Generating efficiency | 88 | % | ZRA |  |  | Volume (mcm) | 0 | 51 | 146 | 294 | 511 | 798 | 1161 | 1615 | 2172 | 2853
Maximum turbine flow | 1220 | cms |  | necessary to meet capacity rating |  | Elevation (m) | 620 | 640 | 660 | 680 | 700 | 720 | 740 | 760 | 780 | 800
Projected reservoir storage capacity | 1680 | mcm | ZRA
Surface area | 25.6 | km2 | ZRA
Volume-elevation curve | see table
Reservoir elevation when full | 762 | m | ZRA | Eurconsult has same head
Tailwater elevation | 596 | m | ZRA
Net head | 166 | m
Devil's Gorge
Owner/Developer | ZRA
Estimated date of commissioning | 2017 |  | SAPP TW2 input
Estimated annual production | 5604 | GWh | ZRA |  | 467
Estimated installed capacity | 1240 | MW | ZRA | 620 MW on each side (MEWD says 500) | 0.51591 | [17 empty] | full at 592
Availability | 93 | % |  |  |  | Volume (mcm) | 83.6 | 153.5 | 384.2 | 760 | 1001.8 | 2040 | 2995.1 | 4182.3 | 5643.2 | 7443.1 | 9662.7 | 12218.2 | 15853.3 | 19560.4 | 23267.5 | 28547.3 | 33947.1 | 83.6 | 468
Generating efficiency | 88 | % | ZRA |  |  | Elevation (m) | 468 | 476 | 484 | 492 | 500 | 508 | 516 | 524 | 532 | 540 | 548 | 556 | 564 | 572 | 580 | 588 | 596 | 153.5 | 476
Maximum turbine flow | 1515 | mcm | [21 empty] | 384.2 | 484
Projected reservoir storage capacity | 31200 | mcm | ZRA |  |  | Area (km2) | 8.8 | 21.5 | 37 | 56.8 | 80 | 104.3 | 132.7 | 165.4 | 203.1 | 246.7 | 297.3 | 352.9 | 424.6 | 497 | 570 | 666 | 762 | 760 | 492
Surface area | 710 | km2 | ZRA | Euroconsult says 762 | [19 empty] | 1001.8 | 500
Volume-elevation curve | see table | [22 empty] | 2040 | 508
Reservoir elevation when full | 592 | m | ZRA | [20 empty] | 2995.1 | 516
Tailwater elevation | 488.5 | m | ZRA | [20 empty] | 4182.3 | 524
Net head | 103.5 |  |  | Eurconsult has head of 110m | [19 empty] | 5643.2 | 532
Mupata - NOT USED | [23 empty] | 7443.1 | 540
Owner/Developer | ZRA | [22 empty] | 9662.7 | 548
Estimated date of commissioning | 2018 |  | SAPP TW2 input | [20 empty] | 12218.2 | 556
Estimated annual production | 7570 | GWh | ZRA |  | 3785 | [18 empty] | 15853.3 | 564
Estimated installed capacity | 1000 | MW | ZRA | 500 MW each side (MEWD says 543) | 0.86416 | [18 empty] | 19560.4 | 572
Availability | 93 | % | [21 empty] | 23267.5 | 580
Generating efficiency | 88 | % | ZRA | [20 empty] | 28547.3 | 588
Projected reservoir storage capacity | 20400 | mcm | ZRA |  |  |  | 556: full | 33947.1 | 596
Surface area | 1250 | km2 | ZRA |  |  | Elevation (m) | 350 | 354 | 358 | 362 | 366 | 370 | 372 | 374 | 376 | 378 | 380 | 406
Volume-elevation curve | see table |  |  |  |  | Area (km2) | 90 | 170 | 295 | 460 | 620 | 785 | 865 | 940 | 1025 | 1105 | 1190 | 2630
Reservoir elevation when full | 381 | m | ZRA |  |  | Volume (mcm) | 800 | 1600 | 2800 | 4300 | 6400 | 8800 | 10300 | 11900 | 13800 | 16000 | 18500 | 64700
Tailwater elevation | 326 | m | ZRA
Net head | 55 | m
Zimbabwe
Kariba South Bank Extension
Owner
Estimated date of commissioning | 2015 |  | SAPP TW2 input
Estimated additional annual production | 1183 | GWh | Nexant (2007)
Estimated additional installed capacity | 300 | MW | Euroconsult and SAPP 2012 hydro |  | 0.45015
Estimated availability (net of planned and forced outages) | 93% | % |  | default value from Nexant 2007
Generating efficiency | 88% | % |  | as per Kariba South original
Maximum turbine flow | 425 | cms |  | estimated to match rated capacity
Tailwater elevation |  | m |  | as per Kariba South existing
Malawi
Kapichira II
Owner | Escom
Estimated annual production | 469 | GWh |  | estimate same as Kapichira I
Estimated installed capacity | 64 | MW | Euroconsult Mott McDonald 2007
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Maximum turbine flow |  | cms
Fixed head height | 54 | m | Euroconsult Mott McDonald 2007 (Annex 2)
Lower Fufu
Owner | Escom
Estimated annual production | 570 | GWh | Euroconsult Mott McDonald 2007
Estimated installed capacity | 90 | MW | Euroconsult Mott McDonald 2007
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Maximum turbine flow |  | cms
Fixed head height | 336 | m | Euroconsult Mott McDonald 2007
Songwe
Owner | Escom
Estimated annual production | 930 | GWh | Euroconsult Mott McDonald 2007
Estimated installed capacity | 150 | MW | Euroconsult Mott McDonald 2007
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Maximum turbine flow |  | cms
Fixed head height |  | m
Kholombidzo
Owner | Escom
Esimated date of commissioning |  | year
Estimated annual production |  | GWh
Estimated installed capacity | 100 | MW | AfDB 2013
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Maximum turbine flow | 300 | cms | WB MSIOA
Fixed head height |  | m
Mpatamanga
Owner | Escom
Generator data
Estimated annual production |  | GWh
Estimated installed capacity | 310 | MW | SAPP Input to Second Team Workshop Aug 2012
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Maximum turbine flow |  | cms
Fixed head height |  | m
Nachimbeya
Owner | Escom |  |  | no info in the Eurconsult study
Estimated annual production |  | GWh |  | other than location
Estimated installed capacity |  | MW
Estimated availability (net of planned and forced outages) |  | %
Generating efficiency |  | %
Maximum turbine flow |  | cms
Fixed head height |  | m
North Rumphi
Owner | Escom
Estimated annual production |  | GWh |  | no capacity info in Euroconsult, only location
Estimated installed capacity |  | MW |  | and dam size
Estimated availability (net of planned and forced outages) |  | %
Generating efficiency |  | %
Maximum turbine flow |  | cms
Fixed head height |  | m
Tanzania
Masigira
Owner | TANESCO
Estimated annual production | 630 | GWh | Eurconsult Mott McD 2007
Estimated installed capacity | 118 | MW | Eurconsult Mott McD 2007 | avg flow 40.3 cms | 0.60947
Estimated availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Fixed head height | 238 | m | Eurconsult Mott McD 2007
Rumakali
Owner | TANESCO |  |  | reservoir only 13km2 so treated as ROR
Estimated annual production | 1320 | GWh | Eurconsult Mott McD 2007
Estimated installed capacity | 222 | MW | Eurconsult Mott McD 2007 | avg flow 13.1 cms | 0.67876
Esatimted availability (net of planned and forced outages) | 93 | % |  | default from Nexant 2007
Generating efficiency | 90 | % |  | default from USBR 2005
Net Head |  | m |  | Euroconsult say 1260!

## summary
Note - detailed sources given in "existing" and "future" sheets
Plant Name | Country | River | Status | Type | Owner | Installed capacity | Average annual generation | Average Head | Reservoir capacity | Surface area when full | Reservoir elevation when full | Tail elevation | Availa-bility | Gen effici-ency | Net evap | Long | Latitude | Dam Height | Dam Length | Catch-ment area | MSIOA sub-basin | Avg flows | Commis-sion
[6 empty] | MW | GWh | m | M m3 | km2 | m amsl | m amsl | % | % | mm/mo | deg E | deg S | m | m | km2 |  | cms | year
Cahora Bassa | Mozambique | Zambezi | Existing | Storage | HCB | 2075 | 15500 | 116 | 65000 | 2670 | 326 | 202 |  |  |  | 32.755 | -15.588 | 171 | 303 | 900000 | 2,4,13 | 2800 | 1976-77
Kafue Gorge Upper | Zambia | Kafue | Existing | Storage | ZESCO | 990 | 5034 | 394 | 785 | 805 | 976.6 | 581.9 | [10 empty] | 1968
Kariba North Bank | Zambia | Zambezi | Existing | Storage | ZESCO | 720 | 3282 | 95 | 64798 | 5577 | 488.5 | 384-405 |  |  |  | 29 | -17 | 128 | 617 | 663800 | 6,8,13 |  | 1959
Victoria Falls | Zambia | Zambezi | Existing | RoR | ZESCO | 108 | 662 | 112.7 | N/A | N/A | N/A | [11 empty] | 1972
Mulungushi | Zambia | Mulungushi | Existing | Storage | LHPC | 20 | 80 | 325 |  | 31 | [5 empty] | 28.833 | -14.717 | 40 | 50 |  | 5 |  | 1955
Lunsemfwa | Zambia | Lunsemfwa | Existing | Storage | LHPC | 18 | 113 | 380 |  | 45 | [5 empty] | 29.1 | -14.483 | 80 | 500 |  | 5 |  | 1944
Itezhi-tezhi Reservoir | Zambia | Kafue | Existing | Storage | ZESCO |  |  | 40 | 5624 | 374 | 1029.5 | [11 empty] | 1977
Kariba South | Zimbabwe | Zambezi | Existing | Storage | ZESA | 750 | 4000 | 95 | 64798 | 5577 | 488.5 |  |  |  |  | 29 | -17 | 128 | 617 | 663800 | 6,8,13 | 1730 | 1958
Nkula Falls A | Malawi | Shire | Existing | RoR | ESCOM | 24 | 161 | 52 | N/A | N/A | N/A |  |  |  |  | 34.833 | -15.517 | 21 | 360 | 136200 | 3 | 420 | 1966
Nkula Falls B | Malawi | Shire | Existing | RoR | ESCOM | 100 | 575 | 57 | N/A | N/A | N/A |  |  |  |  | 34.833 | -15.517 | 21 | 360 | 136200 | 3 | 420 | 1981
Tedzani I & II | Malawi | Shire | Existing | RoR | ESCOM | 40 | 276 | 37 | N/A | N/A | N/A |  |  |  |  | 34.767 | -15.55 |  |  | 136200 | 3 | 420 | 1977
Tedzani III | Malawi | Shire | Existing | RoR | ESCOM | 52 | 312 | 42 | N/A | N/A | N/A |  |  |  |  | 34.767 | -15.55 |  |  | 136200 | 3 | 420 | 1995
Kapichira I | Malawi | Shire | Existing | RoR | ESCOM | 64 | 427 | 54 | N/A | N/A | N/A |  |  |  |  | 34.75 | -15.883 | 26 | 380 | 136200 | 3 | 420 | 2000
Mphanda Nkuwa | Mozambique | Zambezi | Planned | RoR | Mozambique | 1500 | 8600 | 67 | 2324 | 97 | 207 | 140 |  |  |  | 33.25 | -15.8 | 85 | 400 | 929000 | 2,4,13 | 3370 | 2018
Cahora Bassa North | Mozambique | Zambezi | Planned | Storage | HCB | 1245 | 2835 | 116 | existing storage | [6 empty] | 32.755 | -15.588 | 171 | 303 | 900000 | 2,4,13 | 2800 | 2017
Boroma | Mozambique | Zambezi | Studied | RoR | EdM | 160 | 1167.5676 | 17 | N/A |  | N/A |  |  |  |  | 33.45 | -16 | 38 | 280 | 938000 | 2,4-13 | 3370
Lupata | Mozambique | Zambezi | Studied | RoR | EdM | 550 | 4171.2538 | 27 | N/A |  | N/A |  |  |  |  | 34 | -16.633 | 47 | 350 | 1017000 | 2,4-13 | 3600
Ancuaze-Sinjal | Mozambique | Zambezi | Studied | RoR | EdM | 330 | 2230 | 13 | N/A |  | N/A |  |  |  |  | 34.85 | -17.017 | 20 | 1000 | 1017000 | 2,4-13 | 3600
Ancuaze-Sinjal | Mozambique | Zambezi | Studied | RoR | EdM | 600 | 4460 | 27 | N/A |  | N/A |  |  |  |  | 34.85 | -17.017 | 20 | 1000 | 1017000 | 2,4-13 | 3600
Chemba | Mozambique | Zambezi | Studied | Storage | EdM | 1040 | 8760 | 43 | 20080.3221 | 1400 | 98 | 55 |  |  |  | 34.867 | -17.01 | 50 | 9500 | 1025000 | 2,4-13 | 3600
Kariba South Ext | Zimbabwe | Zambezi | Planned | Storage | ZESA | 300 | 1183 | 95 | existing storage | [6 empty] | 29 | -17 | 128 | 617 | 663800 | 6,8,12 | 1730 | 2015
Kariba North Bank Extension | Zambia | Zambezi | Planned | Storage | ZESCO | 360 | 380 | 95 | existing storage | [13 empty] | 2013
Kafue Gorge Lower | Zambia | Kafue | Planned | RoR | ZESCO | 750 | 2400 | 186 | N/A | [13 empty] | 2017
Itezhi-Tezhi | Zambia | Kafue | Studied | Storage | ZESCO/TATA | 120 | 611 | 80 | existing storage | [6 empty] | 26.037 | -15.8 | 65 | 1800 | 105620 | 7 | 284 | 2014
Mkushi | Zambia | Mkushi |  | Storage | LHPC | 65 | 223 | 357
Batoka Gorge | Zam/Zim | Zambezi | Planned | RoR | ZRA | 1600 | 8728 | 166 | 1680 | 25.6 | 762 | 596 |  |  |  | 26.15 | -17.867 |  |  |  | 6,8,13 |  | 2018
Devil's Gorge | Zam/Zim | Zambezi | Studied | Storage | ZRA | 1240 | 5604 | 103.5 | 31200 | 710 | 592 | 488.5 |  |  |  | 26.85 | -17.983 |  |  |  | 6,8-13 |  | 2017
Mupata | Zam/Zim | Zambezi |  | Storage | ZRA | 1000 | 7570 | 55 | 20400 | 1250 | 381 | 326 | [10 empty] | 2018
Lunsemfwa Ext | Zambia | Lunsemfwa | Planned | Storage | LHPC | 55 | 462 | 113 | existing storage
Kabompo Gorge | Zambia | Kabompo | Planned | Storage | CEC | 34 | 176 | 160 | 289 | 28 | [9 empty] | 2300
Kapichira II | Malawi | Shire | Planned | RoR | ESCOM | 64 | 469 | 54 | N/A | 2 | N/A |  |  |  |  | 34.75 | -15.883 | 26 | 380 | 136200 | 3 | 420 | 2013
Kholombidzo | Malawi | Shire | Planned | RoR | ESCOM | 100 |  |  | N/A | N/A | N/A |  |  |  |  | 34.9 | -15.383 | 30 |  |  | 3
Nachimbeya | Malawi | Shire | Planned | RoR | ESCOM | ? |  |  | N/A | N/A | N/A |  |  |  |  | 34.867 | -15.433 |  |  |  | 3
Mpatamanga | Malawi | Shire | Planned | RoR | ESCOM | 310 |  |  | N/A | N/A | N/A |  |  |  |  | 34.733 | -15.717 | 60 |  |  | 3 |  | 2018
5.8 | Mozambique | Revubue | Studied | Storage | EdM | 36 | 155 | 71 | [7 empty] | 33.917 | -15.417 | 90 | 450 | 8245 | 2 | 32
5.9 | Mozambique | Revubue | Studied | RoR | EdM | 110 | 310 | 155 | N/A |  | N/A |  |  |  |  | 33.917 | -15.583 | 35 | 300 | 8380 | 2 | 33
5.13 | Mozambique | Revubue | Studied | Storage | EdM | 85 | 380 | 99 | [7 empty] | 33.75 | -15.917 | 65 | 660 | 14555 | 2 | 62
7.6 | Mozambique | Luia | Studied | Storage | EdM | 267 | 600 | 90 | [7 empty] | 32.917 | -15.5 | 110 | 480 | 27111 | 2 | 138
7.11 | Mozambique | Capoche | Studied | Storage | EdM | 60 | 250 | 88 | [7 empty] | 32.8 | -15.25 | 100 | 400 | 12453 | 2 | 53
Ruo | Mozambique | Ruo/Shire | Concept |  | EdM | 100
Lower Fufu | Malawi | South Rukuru | Planned | RoR | ESCOM | 90 | 570 | 336 | N/A | N/A | N/A | 90 |  |  |  | 34.25 | -10.7 | 17 | 160 | 11993 | 3 | 37.1 | 2015
Masigira | Tanzania | Ruhuhu | Studied | RoR | TANESCO | 118 | 630 | 238 | N/A | N/A | N/A |  |  |  |  | 34.15 | -9.717 | 35 | 700 | 2680 | 3 | 40.3
Rumakali | Tanzania | Rumakali | Studied | Storage | TANESCO | 222 | 1320 |  | N/A | N/A | N/A |  |  |  |  | 34 | -9.317 | 70 | 770 | 414 | 3 | 13.1
North Rumphi | Malawi | North Rumphi | Studied |  | ESCOM | [10 empty] | 34.217 | -10.633 | 8 | 60 | 690 | 3 | 12.9
Songwe | Malawi | Songwe | Identified |  | ESCOM | 150 | 930 | [8 empty] | 33.46 | -9.62 |  |  |  | 3
Upper Fufu | Malawi | South Rukuru | Identified | RoR |  | 70-145
Henga Valley | Malawi | South Rukuru | Identified | RoR |  | 20-40
Sources (incidated by the color of the text)
Euroconsult, and Mott MacDonald. Integrated Water Resources Management Strategy and Implementation Plan for the Zambezi River Basin. Final Report, Rapid Assessment. Gaborone, Botswana and Lusaka, Zambia: South African Development Community Water Division and Zambezi River Authority, December 2007. Table A3.1 p. 173
Burian, Martin, Peter Zhou, Francis Masawi, Francis Yamba, and Florian Baumgard. Analysis of Grid Emission Factors for the Electricity Sector in Sub-Saharan Africa. Roskilde, Denmark: UNEP Risoe Centre, 2012
SAPP 2012 Hydropower supply and demand as at 2011 (May 2012 from SAPP CC - Maviya)
Nexant 2007 Study
MEWD 2010 Zambia Power Development Master Plan 2010-2030
SAPP Input to Second Team Workshop Aug 2012
Malawi HPP presentation
EDM Statistical Summary Report 2011
Beilfuss 2001 Vol 4
ZRA
Combined Plants in Modelling
HPP 5.8-9-13 | Mozambique | Revubue | Studied
7.6-11 | Mozambique | Luia & Capoche | Studied
Luns_Mulung | Zambia | Lunsemfwa | Existing | combines Lunsemfwa and Mulugushi
Small Plants not included in analysis
Lusiwasi | Zambia | Lusiwasi | Existing | Storage | ZESCO | 12 |  | 530 |  | 8 | [5 empty] | 31.1 | -13.033 | 7 | 300 |  | 5 | 2.5 |  | ZESCO
Lusiwasi Ext | Zambia | Lusiwasi | Planned | Storage | ZESCO | 40 |  | 530 |  | 8 | [5 empty] | 31.1 | -13.033 | 7 | 300 |  | 5 | 2.5
Wovwe | Malawi | Wovwe | Existing | RoR | ESCOM | 5 |  | 510 | N/A | N/A | N/A |  |  |  |  | 34.15 | -10.35 |  |  | 165 | 3 | 1 | 1995 | ESCOM
Plants outside Zambezi River Basin
Kalungwishi | includes two sub-projects |  |  |  |  | 218
Kabwelume Falls | Zambia | Kalungwishi/Congo |  | Storage | Lunzua Power Authority | 62
Kundabwika Falls | Zambia | Kalungwishi/Congo |  | Storage | Lunzua Power Authority | 101
Mumbotuta Falls | Zambia | Luapula/Congo |  | RoR? | CEC? | 301
Corumana | Mozambique | Incomati |  | storage |  | 12 | 37 | [15 empty] | 1975
Mavuzi | Mozambique | Buzi |  | storage |  | 50 | 237 | [15 empty] | 1975
Chicamba | Mozambique | Buzi |  | Storage |  | 50 | 79 | [15 empty] | 1975
Massingir | Mozambique | Limpopo | Planned | storgage | Agua Imara/EdM | 27
Lurio | Mozambique | Lurio | Feasibility | RoR | EdM | 120 | no firm power
Moamba Major | Mozambique | Southern Moz | Feasibility | Storage | EdM | <10
Alto Malema | Mozambique | Malema/Lurio | Feasibility | Storage | Agua Imara/EdM | 60
Fossil Fuel plants
Ngana | Malawi |  |  | Planned |  | 300 | [16 empty] | 2016
Note on F5: Randall Spalding-Fecher: Beilfuss and MSIOA have reservoir parameters
Note on F46: Randall Spalding-Fecher: treat as RoR given very small reservoir size
Note on H4: Randall Spalding-Fecher: all data confirmed by HCB
Note on H17: Randall Spalding-Fecher: data on this line from HMNK or confirmed by them
Note on J72: Randall Spalding-Fecher: must be mistake in original data source, same for others in italics
Note on Y6: Randall Spalding-Fecher: Beilfuss and Brown 2010

## Zambia
Zambia Hydropower Facilities |  |  | 2010 | 2010
Plant Name | River/ Location | Type | Installed capacity | Generation | commision
|  |  | MW | GWh | year
ZESCO
Kafue Gorge Upper | Kafue | RoR | 990 | 6788 | 1968
Kariba North Bank | Zambezi | Storage | 720 | 2766 | 1976
Victoria Falls | Zambezi | RoR | 108 | 722 | 1968-72
Lusiwasi | Lusiwasi | Storage | 12
Musonda Falls | Luapula | RoR | 5
Chishimba Falls | N. Province | RoR | 6
Lunzua River | N. Province | RoR | 0.75
Lunsemfwa
Mulungushi | Mulungushi | Storage | 20 | 329 | 1955
Lusemfwa | Lunsemfwa | Storage | 18 |  | 1944
Total |  |  | 1879.75
Diesel facilities owned by ZESCO
Plant Name | Installed capacity
MW
Mwinilunga | 1.36
Kabompo | 1.16
Zambezi | 0.96
Mufumbwe | 0.4
Luangwa | 1.28
Lukulu | 0.512
Chama | 0.263
Kaputa | 0.55
Chavuma | 0.8
Total | 7.285
Euroconsult, and Mott MacDonald. Integrated Water Resources Management Strategy and Implementation Plan for the Zambezi River Basin. Final Report, Rapid Assessment. Gaborone, Botswana and Lusaka, Zambia: South African Development Community Water Division and Zambezi River Authority, December 2007. Table A3.1 p. 173
Burian, Martin, Peter Zhou, Francis Masawi, Francis Yamba, and Florian Baumgard. Analysis of Grid Emission Factors for the Electricity Sector in Sub-Saharan Africa. Roskilde, Denmark: UNEP Risoe Centre, 2012
SAPP 2011 Report (May 2012 from SAPP CC)
Nexant Study
MEWD 2010 Zambia Power Development Master Plan 2010-2030
SAPP Input to Second Team Workshop
Plant Name | River/ Location | Owner | Type | Additional capacity | Est. start year
MW
Extensions/Brownfield
Kariba North Bank Extension | Zambezi | ZESCO | Storage | 360 | 2013 | China Ex-Im Bank, Sinohydro is EPC contractor
Lusiwasi Ext | Lusiwasi River | private | Storage | 50
Itezhi-Tezhi | Kafue River | ZESCO/TATA | Storage | 120 | 2014 | Sinohydro is EPC contractor
Lunsemfwa Ext | Lunsemfwa | LHPC | Storage | 55 |  | Africa E J mentions 200MW
Greenfield plants
Kafue Gorge Lower | Kafue River | ZESCO | RoR | 750 | 2017 | China Africa Dev Fund, Sinohydro
Kabompo Gorge | Kabompo River | CEC/TATA | Storage | 34 | 2015
Batoka Gorge | Zambezi | ZRA | RoR | 1600 | 2018
Devil's Gorge | Zambezi | ZRA | Storage | 1200 | 2017
Mpata Gorge | Zambezi | ZRA | Storage | 1200 | 2018
Kabwelume Falls | Kalungwishi/Congo | Lunzua Power Authority | Storage | 83 | 2016
Kundabwika Falls | Kalungwishi/Congo | Lunzua Power Authority | Storage | 135 | 2016
Mumbotuta Falls | Luapula/Congo | CEC | RoR | 301
Mambilima Falls I & II | Luapula/Congo |  | RoR | 326
Mutinondo/Luchenene | Munyamadzi/Luangwa | Power Min | RoR | 70 | 2017
Mkushi | Mkushi | LHPC | Storage | 65
Coal
Maamba |  | Nava Bharat, ZCCM-IH, CEC, ZESCO |  | 500 | 2014 | being built in 150MW increments, ZESCO reducing share
Ndola Energy? |  |  |  | 56 |  | mentioned at SAPP meeting
African Energy Journal June 2011
Note on F49: Randall Spalding-Fecher: 800 for each country
Note on F50: Randall Spalding-Fecher: split between two countries
Note on F51: Randall Spalding-Fecher: split between two countries

## Moz
Mozambique Hydropower Facilities |  |  | 2010 | 2010
Plant Name | River/ Location | Type | Installed capacity | Generation | Commision
|  |  | MW | GWh | year
EdM
Corumana | Incomati | storage | 12 | 37 | 1975 | Not in Zambezi
Mavuzi | Buzi | storage | 50 | 237 | 1975 | Not in Zambezi
Chicamba | Buzi | Storage | 50 | 79 | 1975 | Not in Zambezi
HCB
Cahora Bassa | Zambezi | Storage | 2075 | 16290 | 1977 | source of GWh?
Total |  |  | 2187
Thermal facilities
Plant Name | Capacity (MW) | Year installed | Fuel
Aggreko/Shanduka
Ressano Garcia | 107 | 2012 | Gas | http://africa.aggreko.com/news-events/press-releases/power-station-mozambique/
EdM
Operational
Temane | 3.87 | 2006 | Gas
Emergency use only
Beira | 12 | 1983 | Gas
Ibane Nova | 2.2 | 1999 | Diesel
Maputo | 30 | 1973 | Gas
Maputo | 23 | 1991 | Gas
Nampula | 5.2 | 1965 | Diesel
Quelimane | 6.8 | 1980 | Diesel
http://www.hcb.co.mz/eng/Empresa/Datas-Relevantes + personal comm Suleiman Combo
EdM Statistical Report 2009
Euroconsult, and Mott MacDonald. Integrated Water Resources Management Strategy and Implementation Plan for the Zambezi River Basin. Final Report, Rapid Assessment. Gaborone, Botswana and Lusaka, Zambia: South African Development Community Water Division and Zambezi River Authority, December 2007. Table A3.1 p. 173
Burian, Martin, Peter Zhou, Francis Masawi, Francis Yamba, and Florian Baumgard. Analysis of Grid Emission Factors for the Electricity Sector in Sub-Saharan Africa. Roskilde, Denmark: UNEP Risoe Centre, 2012
SAPP 2011 Report (May 2012 from SAPP CC)
news article on Aggreko
New power plants for Mozambique
Plant Name | River/ Location | Developer | Type | Additional capacity | Status | date from EDM | from SAPP 2011 | from SAPP 2008
MW
Extensions/Brownfield
Cahora Bassa North | Zambezi | HCB | Storage | 1245 | Planned | >2019 | 2018 | 2015
Mavuzi 2&3 | Mavuzi | EdM | storage | 60 | Concept
Greenfield plants
Mphanda Nkuwa | Zambezi | Government of Mozambique | RoR | 1500 | Planned | 2018 | 2017 | 2015
Massingir | Limpopo | Agua Imara/EdM | storgage | 27 | Planned | N.D. |  | 2009
Lurio | Lurio | EdM+private | RoR | 120 | Feasibility | N.D. | 2015 | 2012
Moamba Major | Southern Moz | EdM | Storage | <10 | Feasibility
Alto Malema | Malema/Lurio | Agua Imara/EdM | Storage | 60 | Feasibility | N.D.
Boroma | Zambezi | EdM+private | RoR | 200 | Feasibility | N.D. | 2018
Lupata | Zambezi | EdM+private | RoR | 600 | Feasibility | N.D. | 2017
Ruo |  | EdM |  | 100 | Concept | N.D. | 2017
Ancuaze-Sinjal | Zambezi | EdM | RoR | 330 | Concept
Ancuaze-Sinjal | Zambezi | EdM | RoR | 600 | Concept
Gas | Location
Ressano Garcia | Ressano Garcia, Maputo Province | Sasol New Energy/EdM |  | 140 | Planned | 2013
Kuvaninga | Chokwe, Gaza | Enventure/Shanduka |  | 44 | under contruction |  | http://enventurepartners.com/portfolio/in-construction/kuvaninga-mozambique/
Coal
Moatize | Tete Province | Vale (Brazil) |  | 300 | Planned | 2015 |  | 2015 | 2000 | larger capacity cited in http://www.gasandoil.com/oilaround/2011/10/mozambique-government-approves-jspls-coal-fired-power-plant (2011)
Benga | Tete Province | Rio Tinto |  | 500 | Planned | 2017 |  | 2012 | 2000 | and in http://www.esi-africa.com/node/14995 (2012)
JSPL | Tete Province | Jindal Steel & Power |  | 2640 |  | 2015 |  |  |  | maybe only first units by 2015
Ncondezi | Tete Province | Ncondezi Coal |  | 300/1800 |  | 2017 for 300
EDM Statistical Report 2011 + personal communication
EdM personal communication
Euroconsult, and Mott MacDonald. Integrated Water Resources Management Strategy and Implementation Plan for the Zambezi River Basin. Final Report, Rapid Assessment. Gaborone, Botswana and Lusaka, Zambia: South African Development Community Water Division and Zambezi River Authority, December 2007. Table A3.1 p. 173
http://www.gasandoil.com/oilaround/2011/10/mozambique-government-approves-jspls-coal-fired-power-plant (Oct 2011)
http://www.esi-africa.com/node/14995 (July 2012)
SAPP 2011 hydropower supply and demand
Note on J36: Randall Spalding-Fecher: this also had Temane Gas 750MW by 2011, which was never completed

## future table
Plant Name | Country | River | Owner | Installed capacity | Average annual generation | Reservoir capacity | Surface area when full | Reservoir elevation when full | Average Head | Tail elevation | Commis-sion | Status | Type
|  |  |  | MW | GWh | M m3 | km2 | m amsl | m | m amsl | year
Cahora Bassa North | Mozambique | Zambezi | HCB | 1245 | 2835 | existing storage | 0 | 0 | 116 | 0 | 2017 | Planned | Storage
Mphanda Nkuwa | Mozambique | Zambezi | Mozambique | 1500 | 8600 | 2324 | 97 | 207 | 67 | 140 | 2018 | Planned | RoR
Batoka Gorge | Zam/Zim | Zambezi | ZRA | 1600 | 8728 | 1680 | 25.6 | 762 | 166 | 596 | 2018 | Planned | RoR
Itezhi-Tezhi | Zambia | Kafue | ZESCO/TATA | 120 | 611 | existing storage | 0 | 0 | 80 | 0 | 2014 | Studied | Storage
Devil's Gorge | Zam/Zim | Zambezi | ZRA | 1240 | 5604 | 31200 | 710 | 592 | 103.5 | 488.5 | 2017 | Studied | Storage
Mupata | Zam/Zim | Zambezi | ZRA | 1000 | 7570 | 20400 | 1250 | 381 | 55 | 326 | 2018 | 0 | Storage
Kariba South Ext | Zimbabwe | Zambezi | ZESA | 300 | 1183 | existing storage | 0 | 0 | 95 | 0 | 2015 | Planned | Storage
Kariba North Bank Extension | Zambia | Zambezi | ZESCO | 360 | 380 | existing storage | 0 | 0 | 95 | 0 | 2013 | Planned | Storage
Kafue Gorge Lower | Zambia | Kafue | ZESCO | 750 | 2400 | N/A | 0 | 0 | 186 | 0 | 2017 | Planned | RoR
Kabompo Gorge | Zambia | Kabompo | CEC | 34 | 176 | 289 | 28 | 0 | 160 | 0 |  | Planned | Storage
Lunsemfwa Ext | Zambia | Lunsemfwa | LHPC | 55 | 462 | existing storage | 0 | 0 | 113 | 0 |  | Planned | Storage
Boroma | Mozambique | Zambezi | EdM | 160 | 1167.5676 | N/A | 0 | N/A | 17 | 0 |  | Studied | RoR
Lupata | Mozambique | Zambezi | EdM | 550 | 4171.2538 | N/A | 0 | N/A | 27 | 0 |  | Studied | RoR
Ancuaze-Sinjal | Mozambique | Zambezi | EdM | 330 | 2230 | N/A | 0 | N/A | 13 | 0 |  | Studied | RoR
Ancuaze-Sinjal | Mozambique | Zambezi | EdM | 600 | 4460 | N/A | 0 | N/A | 27 | 0 |  | Studied | RoR
Chemba | Mozambique | Zambezi | EdM | 1040 | 8760 | 20080.3221 | 1400 | 98 | 43 | 55 |  | Studied | Storage
5.9 | Mozambique | Revubue | EdM | 110 | 310 | N/A | 0 | N/A | 155 | 0 |  | Studied | RoR
Masigira | Tanzania | Ruhuhu | TANESCO | 118 | 630 | N/A | N/A | N/A | 238 | 0 |  | Studied | RoR
Kapichira II | Malawi | Shire | ESCOM | 64 | 469 | N/A | 2 | N/A | 54 | 0 | 2013 | Planned | RoR
Lower Fufu | Malawi | South Rukuru | ESCOM | 90 | 570 | N/A | N/A | N/A | 336 | 90 | 2015 | Planned | RoR
Kholombidzo | Malawi | Shire | ESCOM | 100 |  | N/A | N/A | N/A | 0 | 0 |  | Planned | RoR
Nachimbeya | Malawi | Shire | ESCOM | ? |  | N/A | N/A | N/A | 0 | 0 |  | Planned | RoR
Mpatamanga | Malawi | Shire | ESCOM | 310 |  | N/A | N/A | N/A | 0 | 0 | 2018 | Planned | RoR
Mkushi | Zambia | Mkushi | LHPC | 65 | 223 | 0 | 0 | 0 | 357 | 0 |  | 0 | Storage
Upper Fufu | Malawi | South Rukuru | 0 | 70-145 |  | 0 | 0 | 0 | 0 | 0 |  | Identified | RoR
Henga Valley | Malawi | South Rukuru | 0 | 20-40 |  | 0 | 0 | 0 | 0 | 0 |  | Identified | RoR
5.8 | Mozambique | Revubue | EdM | 36 | 155 | 0 | 0 | 0 | 71 | 0 |  | Studied | Storage
5.13 | Mozambique | Revubue | EdM | 85 | 380 | 0 | 0 | 0 | 99 | 0 |  | Studied | Storage
7.6 | Mozambique | Luia | EdM | 267 | 600 | 0 | 0 | 0 | 90 | 0 |  | Studied | Storage
7.11 | Mozambique | Capoche | EdM | 60 | 250 | 0 | 0 | 0 | 88 | 0 |  | Studied | Storage
Ruo | Mozambique | Ruo/Shire | EdM | 100 |  | 0 | 0 | 0 | 0 | 0 |  | Concept | 0
Rumakali | Tanzania | Rumakali | TANESCO | 222 | 1320 | N/A | N/A | N/A | 0 | 0 |  | Studied | Storage
North Rumphi | Malawi | North Rumphi | ESCOM | 0 |  | 0 | 0 | 0 | 0 | 0 |  | Studied | 0
Songwe | Malawi | Songwe | ESCOM | 150 | 930 | 0 | 0 | 0 | 0 | 0 |  | Identified | 0
plant italics are not modelled due to lack of data
Sources (incidated by the color of the text)
Euroconsult, and Mott MacDonald. Integrated Water Resources Management Strategy and Implementation Plan for the Zambezi River Basin. Final Report, Rapid Assessment. Gaborone, Botswana and Lusaka, Zambia: South African Development Community Water Division and Zambezi River Authority, December 2007. Table A3.1 p. 173
Burian, Martin, Peter Zhou, Francis Masawi, Francis Yamba, and Florian Baumgard. Analysis of Grid Emission Factors for the Electricity Sector in Sub-Saharan Africa. Roskilde, Denmark: UNEP Risoe Centre, 2012
SAPP 2012 Hydropower supply and demand as at 2011 (May 2012 from SAPP CC - Maviya)
Nexant 2007 Study
MEWD 2010 Zambia Power Development Master Plan 2010-2030
SAPP Input to Second Team Workshop Aug 2012
Malawi HPP presentation
EDM Statistical Summary Report 2011
Small Plants not included in analysis
Lusiwasi | Zambia | Lusiwasi | ZESCO | 12 | 0 | 0 | 8 | 0 | 530 | 0 | 0 | Existing | Storage
Lusiwasi Ext | Zambia | Lusiwasi | ZESCO | 40 | 0 | 0 | 8 | 0 | 530 | 0 | 0 | Planned | Storage
Wovwe | Malawi | Wovwe | ESCOM | 5 | 0 | N/A | N/A | N/A | 510 | 0 | 1995 | Existing | RoR
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plants outside Zambezi River Basin
Kalungwishi | includes two sub-projects | 0 | 0 | 218 | 0 | [5 empty] | 0 | 0 | 0
Kabwelume Falls | Zambia | Kalungwishi/Congo | Lunzua Power Authority | 62 | 0 | [5 empty] | 0 | 0 | Storage
Kundabwika Falls | Zambia | Kalungwishi/Congo | Lunzua Power Authority | 101 | 0 | [5 empty] | 0 | 0 | Storage
Mumbotuta Falls | Zambia | Luapula/Congo | CEC? | 301 | 0 | [5 empty] | 0 | 0 | RoR?
Corumana | Mozambique | Incomati | 0 | 12 | 37 | [5 empty] | 1975 | 0 | storage
Mavuzi | Mozambique | Buzi | 0 | 50 | 237 | [5 empty] | 1975 | 0 | storage
Chicamba | Mozambique | Buzi | 0 | 50 | 79 | [5 empty] | 1975 | 0 | Storage
Massingir | Mozambique | Limpopo | Agua Imara/EdM | 27 | 0 | [5 empty] | 0 | Planned | storgage
Lurio | Mozambique | Lurio | EdM | 120 | no firm power | [5 empty] | 0 | Feasibility | RoR
Moamba Major | Mozambique | Southern Moz | EdM | <10 | 0 | [5 empty] | 0 | Feasibility | Storage
Alto Malema | Mozambique | Malema/Lurio | Agua Imara/EdM | 60 | 0 | [5 empty] | 0 | Feasibility | Storage
Fossil Fuel plants
Ngana | Malawi | 0 | 0 | 300 | 0 | [5 empty] | 2016 | 0 | Planned

## exist dam
Dam/Plant Name | Country | River | Installed capacity | Commis-sion | Average annual generation | Reservoir capacity | Surface area when full | Reservoir elevation when full | Average Head | Tail elevation
|  |  | MW | year | GWh | M m3 | km2 | m amsl | m | m amsl
Cahora Bassa | Mozambique | Zambezi | 2075 | 1976-77 | 15500 | 65000 | 2670 | 326 | 116 | 202
Kafue Gorge Upper | Zambia | Kafue | 990 | 1968 | 5034 | 785 | 805 | 976.6 | 394 | 581.9
Kariba South | Zimbabwe | Zambezi | 750 | 1958 | 4000 | 64798 | 5577 | 488.5 | 95 | 0 | 0.60883
Kariba North Bank | Zambia | Zambezi | 720 | 1959 | 3282 | 64798 | 5577 | 488.5 | 95 | 384-405 | 0.52036
Victoria Falls | Zambia | Zambezi | 108 | 1972 | 662 | N/A | N/A | N/A | 112.7 | 0
Mulungushi | Zambia | Mulungushi | 20 | 1955 | 80 | 0 | 31 | 0 | 325 | 0
Lunsemfwa | Zambia | Lunsemfwa | 18 | 1944 | 113 | 0 | 45 | 0 | 380 | 0
Itezhi-tezhi Reservoir | Zambia | Kafue | N/A | 1977 | N/A | 5624 | 374 | 1029.5 | 40 | 0
Nkula Falls A | Malawi | Shire | 24 | 1966 | 161 | N/A | N/A | N/A | 52 | 0
Nkula Falls B | Malawi | Shire | 100 | 1981 | 575 | N/A | N/A | N/A | 57 | 0
Tedzani I & II | Malawi | Shire | 40 | 1977 | 276 | N/A | N/A | N/A | 37 | 0
Tedzani III | Malawi | Shire | 52 | 1995 | 312 | N/A | N/A | N/A | 42 | 0
Kapichira I | Malawi | Shire | 64 | 2000 | 427 | N/A | N/A | N/A | 54 | 0

## future yr
Plant | Year of commissioning in each development future
| Business as Usual | Optimistic
Cahora Bassa North | 2022 | 2017
Mphanda Nkuwa | 2022 | 2017
Kariba South Extension | 2018 | 2015
Kariba North Extension | 2014 | 2013
Kafue Gorge Lower | 2022 | 2017
Devil’s Gorge | 2025 | 2017
Batoka Gorge | 2022 | 2018 | y
Kapichira II | 2016 | 2014
Boroma | 2025 | 2020 | y
Lupata | 2025 | 2020 | y
Date in
Ref Scenario